Fire damper BKA-EN

Technical Documentation

The fire damper BKA-EN conforms to the product standard EN 15650.

The BKA-EN has been tested according to EN 1366-2. CE marking and Declaration of performance (DoP) in accordance with the Construction Products Regulation (BauPVO). According to EN 13501-3, the classification is EI 30 (ve, i↔o) S to EI 90 (ve, ho i↔o) S. According to Directive 2014/34/EU, EC Certificate of Con-formity number EPS 09 ATEX 2 153 X, its use in areas subject to explosion hazards is permitted, not only with spring return actuator ExMax-5.10-BF (X10 - X15), including safety tem-perature limiter (ExPro-TT), but also with mechanical trigger via fusible link (manual actuation with or without ATEX limit switch ES-Ex). The fire damper is marked as follows accord-ing to ATEX:

Housing made of galvanised sheet steel - 2-parts -, without circumferential stop profiles for largest possible free cross-section, thermal insulation made of silicate boards, 2 inspec-tion openings on opposite sides. Damper blade made of abrasion-resistant, glass-fibre-reinforced lightweight con-crete with circumferential hose and intumescent seals to meet the cold and hot leakage requirements according to DIN EN 1366-2.

Any accessories that may be required for the respective mounting situation (flexible pieces, suspensions, pole brac-es, etc.) are listed in separate positions of the specification.

For connection to ventilation ducts (one- or two-sided), air flow direction optional.

Connection to smoke detectors with general building super-visory approval possible.

If the smoke alarm system type RMS is used, the additional information in the Technical Documentation must be ob-served.

Installation:

In solid walls, solid ceilings and lightweight partition walls with metal posts and panelling on both sides as classified according to EN 13501-2 or comparable national standards.

With Hilti soft seal system in solid walls and lightweight partition walls with metal post and panelling on both sides as classified according to EN 13501-2 or comparable national standards.

With installation kit type GDA in solid walls; in the area of flexible ceiling connections and only possible for BKA-EN L=375.

With mounting kit type AS-E1 on solid walls; only possible with BKA-EN L=375.

With ERA2 installation frame away from solid walls.

With concrete base in solid ceilings.

With installation frame type ER-A1 in lightweight partition walls with metal posts and panelling on both sides as classified according to EN 13501-2 or comparable national standards.

With installation kit type GDL in lightweight partition walls with metal posts and panelling on both sides as classified according to EN 13501-2 or comparable national standards; in the area of flexible ceiling connections 
(The version of the installation kit type GDL depends on the selected metal post profiles [single stud structure] of the wall and can only be used with BKA-EN L=375).

Directly under solid ceilings with mineral wool inlay in lightweight partition walls with metal posts and panelling on both sides as classified according to EN 13501-2 or comparable national standards.

In lightweight partition walls with metal posts and panelling on one side as classified according to EN 13501-2 or comparable national standards.

At a reduced distance "flange-to-flange" (for installation in solid walls and solid ceilings)

Partial mortar lining (for installation in solid walls with rigid ceiling connection)

Product: SCHAKO TYPE BKA-EN

Declaration of Performance no. DoP-BKA-EN-2021-06-01

Dimensions:

| Width (B): | ……………………..mm |
| --- | --- |
| Height (H): | ……………………..mm |
| Length (L): | 375 / 500 mm |

(Unless stated otherwise, the mechanical model length 500mm and fusible link trigger temperature 72°C will be delivered)

Alternative designs or accessories (at an extra charge) (select as desired)

Model made of stainless steel material no. 1.4301 (V2A)

Model made of stainless steel material no. 1.4571 (V4A; replaceable, non-coated parts are made of stainless steel material no. 1.4301)

Housing with DD coating (solvent-containing two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

  - DD coating inside/outside (replaceable, non-coated parts and the U-profile of the damper blade are made of stainless steel material no. 1.4301)

Thermal release with mechanical fusible link release temperature 98°C (for hot-air heating)

Model marked according to ATEX

Electric limit switch type ES for "OPEN" and/or "CLOSED" position indicators, switching element containing one NC and one NO contact:

ESZ (type ES 1Z: "CLOSED")

ESA (TYPE ES 1A: "OPEN")

EZA (type ES 2: "OPEN" and "CLOSED")

Limit switch type ES-Ex (ATEX) for "OPEN" and/or "CLOSED" position indicators, application in areas subject to explosion hazards:

EXZ (type ES EX 1Z: "CLOSED")

EXA (type ES EX 1A: "OPEN")

EX2 (type ES EX 2: "OPEN" and "CLOSED")

Limit switch ETX (type EasyF-ETX), for connection to SCHAKO signalling and switching bus system EasyBus, the status of the damper position being transferred by radio signal. Additional radio receiver EasyF-RXE required.

ETZ (type EasyF-ETX: "CLOSED")

ETA (type EasyF-ETX: "OPEN")

ETX (type EasyF-ETX: "OPEN" and "CLOSED")

Spring return actuator with thermoelectric trigger mechanism BAT (B10/B11/B20/B21/B32/B33) or temperature monitoring unit (S00/S01/S10/S11/ S20/S21)

Releases at a room temperature of 72°C and an internal duct temperature of 72°C (optionally: 95°C) containing integrated micro switches for indication of damper end positions (24 V drive with connector), assignment of the actuators according to Tabelle 11 page 56:

Type B10 (BFL24-T-ST SO)

B11 (BFL230-T SO)

B20 (BFN24-T-ST SO)

B21 (BFN230-T SO)

B32 (BF24-TN-ST SO)

B33 (BF230-TN SO)

Type S00 (GRA126.1E/SO3)

S01 (GRA326.1E/SO2)

S10 (GNA126.1E/SO3)

S11 (GNA326.1E/SO2)

S20 (GGA126.1E/SO3)

S21 (GGA326.1E/SO2)

Spring return actuator with thermoelectric trigger BAT72TL

Triggers at an internal duct temperature of 72°C (optional: 95°C); integrated microswitches indicate the damper positions; connection to Belimo MP bus systems via communication device is possible. Available for all dimensions.

Type B42 (BF24TL-TN-ST SO; 24V AC/DC)

  - Communication device ZB6 (BKN230-24MP) for connection to Belimo MP bus systems

Electric explosion-protected spring return actuator with safety temperature limiter (ExPro-TT).

- Releases at a room temperature of 72°C and an internal duct temperature of 72°C (optionally: 95°C), end position signalling by integrated auxiliary switches:

  - Type ExMax-5.10-BF (X14 - X15; universal power supply 24 - 240 V AC/DC).

Actuators J10/J11/J20 upon request (assignment according to the BKA-EN dimension)

Pneumatic swivel drive P10/P20/P30 (PND 6 bar, assignment according to the BKA-EN dimensions)

Magnetic clamps MH1 (24 V DC) / MH2 (230 V AC)

Pulse magnets MI1 (24 V DC) / MI2 (230 V AC)

Extension piece type VT, for installation with large wall/ceiling thicknesses; to maintain the minimum distance amin = 50 mm from the open damper blade when mounting the finishing protective grating type ASG, flexible connection piece type FS or duct connection spigot type RS. Extension part made of galvanised profiled sheet steel fitted with connecting flanges, L=180 mm (damper height 200 to 750 mm), L=210 mm (damper height 800 mm).

Product: SCHAKO type VT

Dimensions:

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Extra charge for anticorrosive paint - inside/outside -

  - DD coating (two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

Extra charge for design:

  - Material no. 1.4301 (V2A)

  - Material no. 1.4571 (V4A)

Flexible spigot FS consisting of profiled connection flanges (galvanised sheet steel) with elastic intermediate piece made of polyester fabric PVC-coated on both sides, standard flammable according to EN 13501-1, with welded lip seals (sealing degree C according to EN 13180/EN 1507; temperature-resistant from -20° to 80°C). The flexible part of the spigot (polyester fabric) must have a minimum length of lmin = 100 mm when mounted, resulting in an installation dimension of approx L = 160 mm.

The required equipotential bonding must be carried out on-site according to VDE regulations.  The fire dampers must not be subject to mechanical stress under any circumstances.

Product: SCHAKO type FS

Dimensions:

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Extra charge for connection flanges made of:

  - Material no. 1.4301 (V2A)

  - Material no. 1.4571 (V4A)

Duct connection spigot type RS, for connecting round ventilation ducts to BKA-EN, consisting of joining plate with bores and connecting pipe, galvanised sheet steel.

Product: SCHAKO type RS

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |
| Connection pipe ø (øD) | ……………………mm |

Extra charge for anticorrosive paint - inside and outside -

  - DD coating (two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

Extra charge for design:

  - Material no. 1.4301 (V2A)

  - Material no. 1.4571 (V4A)

Security grille type ASG, for mounting with ventilation duct connection on only one side, wire or punch grille, galvanised sheet steel, mesh width ≤ 20 mm, minimum distance amin = 50 mm from the open damper blade must be taken into account, if necessary, use extension piece type VT.

Product: SCHAKO type ASG

Dimensions:

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Extra charge for anticorrosive paint - inside and outside -

  - DD coating (two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

Extra charge for design:

  - Material no. 1.4301 (V2A)

  - Material no. 1.4571 (V4A)

Position indicator type MSZ, consisting of a galvanised steel cable with clamping nipple and position indicator made. The mechanical position indicator for false ceilings is usable for each mechanically operated BKA-EN with hand lever.

Product: SCHAKO type MSZ

Installation frame type ER-A1, consisting of silicate boards, with fastening material, for installation of the BKA-EN in lightweight partition walls with metal posts and panelling on both sides as classified according to EN 13501-2 or comparable national standards. The ER-A1 installation frame is to be ordered as an accessory (extra charge) – supplied loose or factory-mounted. A circumferential intumescent seal is located in the centre of the installation frame type ER-A1. Fixing lugs are included in delivery.

Product: SCHAKO Installation frame type ER-A1

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

(Unless stated otherwise in the order details, the ER-A1 installation frame will be delivered loose as a mounting kit)

ERA2 installation frame, consisting of silicate boards, for installation away from solid walls. The ERA2 installation frame is to be ordered as an accessory (extra charge) – supplied loose or factory-mounted.

Product: SCHAKO installation frame Type ERA2

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

(Unless stated otherwise in the order details, the ERA2 installation frame will be delivered loose as a mounting kit)

Mounting kit type AS-E1, consisting of joining plate, silicate boards and screen incl. fastening material and mineral wool strips, for installation of the BKA-EN (L=375) directly on solid walls.

The mounting kit type AS-E1 is delivered loose as a mounting kit and can only be used with a BKA-EN with L=375 mm.

The delivered means for wall mounting are suitable for solid walls (concrete ≥ C20/25), for other walls, suitable fastening means must be provided on site.

Product: SCHAKO Mounting kit type AS-E1

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Installation kit type GDA, consisting, among other things, of silicate boards, for installation of the BKA-EN (L=375) in solid walls; wall thickness ≥ 100 mm, in the area of flexible ceiling connections (flexibility/ceiling bending ≤ 20 mm). The installation kit type GDA is delivered loose as a mounting kit and can only be used with a BKA-EN with L=375 mm.

Product: SCHAKO Installation kit type GDA

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Installation kit type GDL, consisting of silicate boards, U-profile and fastening brackets, for installation of BKA-EN (L=375) in lightweight partition walls with metal posts (single stud structure) and panelling on both sides (gypsum-bonded wall boards; wall thickness ≥ 100 mm to ≤ 175 mm) according to classification to EN 13501-2 or comparable national standards, in the area of sliding ceiling connections (sliding/ceiling bending ≤ 20 mm). The installation kit type GDL is only delivered mounted ex works and can only be used with a BKA-EN with L=375 mm.

Product: SCHAKO Installation kit type GDL

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |
| CW/UW (web height) | ……………………mm |

(The version of the installation kit type GDL depends on the web height of the selected metal post profiles [CW/UW; single stud structure] of the wall and must be considered and specified when ordering and selecting it).