Fire-Resistant Damper Model BKA-Ü

Specification texts

Fire-resistant dampers of special design and application are used if, as part of ventilation planning, openings are required in fire-resistant inner walls or ceilings for the air intake, they must be closed in the event of a fire.

The competent building supervisory authority will decide whether the opening is admissible, for example because it differs or in connection with the approval of the fire protection concept.

The required dampers are fire-resistant dampers which are closed in case of fire driven by a suitable smoke detecting triggering device in the event of a fire, thus preventing the propagation of fire and smoke through the component opening. Dampers of this type must not be connected to ventilation ducts in connection with RLT systems in buildings.

The general type approval (aBG) Z-6.50-2012 in its currently valid form, the installation, mounting and operating instructions and the relevant national standards and directives must be observed.

The standard fire-resistant damper BKA-Ü consists of the following components (fitted or wired ex works):

SCHAKO Fire damper BKA-EN, with CE marking and Declaration of Performance (DoP) in accordance with the Construction Products Ordinance, housing made of galvanised sheet steel with spring return actuator 24 V.

SCHAKO Mounting part type EBT, galvanised sheet steel model (painted black matt on the inside).

SCHAKO Finishing protective grating type ASG on both sides, galvanised sheet steel model (operator side: painted black matt).

SCHAKO Extension piece type VT, galvanised sheet steel model, required for H ≥ 400.

SCHAKO Smoke detection system RMS, in compliance

with abZ/aBG No. Z-78.6-58

Installation is performed in interior walls (horizontal position of the damper blade axle) and ceilings. In doing so, the general building supervisory approval (aBG) no. Z-6.50-2012, the Declaration of performance (DoP) of BKA-EN and the general building supervisory approval (abZ) / general type approval (aBG) no. Z-78.6-58 and the associated technical documentation must be observed. For the installation in solid ceilings, the dimensions of BKA-Ü are limited to W and H = 500 mm. For wall installation, the smoke detector (type RMSII-L) must always be installed above (B side) in the assembly part type EBT.

Product:

SCHAKO Type BKA-Ü

General type approval (aBG) no. Z-6.50-2012

Dimensions

Width (B): .................... mm

Height (H): .................... mm

Length (L): 500 mm (standard length refers to BKA-EN)

Alternative designs or accessories (at an extra charge) (select as desired)

Model made of stainless steel material no. 1.4301 (V2A)

Note: EBT painted in black matt on the inside, ASG painted in black matt on operator side

Model made of stainless steel material no. 1.4571 (V4A; replaceable, non-coated parts are made of stainless steel material no. 1.4301)

Note: EBT painted in black matt on the inside, ASG painted in black matt on operator side

Housing with DD coating (solvent-containing two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

DD coating inside and outside (replaceable, non-coated parts and the U-profile of the damper

blade are made of stainless steel material no. 1.4301)

Note: EBT painted in black matt on the inside, ASG painted in black matt on operator side.

Spring return actuator with thermoelectric trigger mechanism BAT (B10/B20/B32) or temperature monitoring unit (S00/S10/S20)

Releases at an ambient temperature of 72°C and an internal duct temperature of 72°C containing integrated micro switches for indication of damper end positions, assignment of the actuators according to Fehler! Verweisquelle konnte nicht gefunden werden. page Fehler! Textmarke nicht definiert.:

    - Type B10 (BFL24-T-ST SO)

B20 (BFN24-T-ST SO)

B32 (BF24-TN-ST SO)

Type S00 (GRA126.1E/SO3)

S10 (GNA126.1E/SO3)

S20 (GGA126.1E/SO3)

Fire-Resistant Damper Model BKA-Ü

Installation frame type ER-A1, consisting of silicate boards, with fastening material, for installation of the BKA-Ü in lightweight partition walls with metal posts and panelling on both sides as classified according to EN 13501-2 or comparable national standards. The ER-A1 installation frame is to be ordered as an accessory (extra charge) – supplied loose or factory-mounted. A circumferential intumescent seal is located in the centre of the installation frame type ER-A1. Fixing lugs are included in delivery.

Product: SCHAKO Installation frame type ER-A1

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

(Unless stated otherwise in the order details, the installation frame type ER-A1 will be delivered loose as a mounting kit)