Fire damper mini-controller BKSYS

Specification text

Fire damper mini-controller BKSYS

Product SCHAKO KG

Fire damper mini-controller BKSYS for control and display of fire damper actuators and limit switches consisting of:

basic module BKSYS-GM1

microprocessor-controlled

with real-time clock, gold cap and ring buffer for control and display of up to:

--- four motorised fire dampers with 24 V AC/DC spring re-turn actuators or

--- four mechanical fire dampers with two limit switches each OPEN/CLOSE or

--- eight mechanical fire dampers with one limit switch each OPEN or CLOSED

The configuration can be selected freely. Visualisation of the statuses by means of green/red Duo LEDs.

With two potential-free fault inputs (ventilation, smoke de-tector, central fire alarm system, etc.) and a potential-free fault output (changeover contact). With test switch for func-tional test incl. runtime monitoring and logging (ring buffer).

Operating voltage 24V AC/DC

Fastening: DIN rail mounting

Dimensions 160 x 90 x 106 mm (WxHxD)

Can be parameterised via USB interface.

The basic module BKSYS-GM1 can be extended with up to three expansion modules BKSYS-EM1 using Plug and Play plug-in connection.

Product: SCHAKO type BKSYS-GM1

expansion module BKSYS-EM1

microprocessor-controlled

For control and display of up to

--- four motorised fire dampers with 24 V AC/DC spring re-turn actuators or

--- four mechanical fire dampers with two limit switches each OPEN/CLOSE or

--- eight mechanical fire dampers with one limit switch each OPEN or CLOSED

The configuration can be selected freely. Visualisation of the statuses by means of green/red Duo LEDs.

With a potential-free fault input (smoke detector, central fire alarm system etc.) and a potential-free fault output (change-over contact). With test switch for functional test. Runtime monitoring and logging (ring buffer) is performed via the basic module as well as the power supply and system con-trol.

Operating voltage 24V AC/DC

Fastening: DIN rail mounting

Dimensions 110 x 90 x 106 mm (WxHxD)

Product: SCHAKO type BKSYS-EM1

ACCESSORIES

Connection socket BKSYS-ADM

for the plug-in connection of spring return actuator 24V AC/DC. With spring-type terminals for the connection of connecting cables to the BKSYS modules. With LED (green) for indication of power supply at BKSYS-ADM.

Product: SCHAKO type BKSYS-ADM

USB-RS232 ADAPTER BKSYS-USB

for connection of a PC to the basic module incl. operation and protocol software as well as the connecting cable (2 m).

Product: SCHAKO type BKSYS-USB

ModBus interface for BKSYS-GM1

Network interface for data transmission from BKSYS to other systems.

--- Serial interface to EIA-485 standard, galvanically isolated

--- RTU transmission protocol

--- Power supply from and communication connection to basic module via plug-in connector

--- Signalling of received data packets by green flashing of a two-colour LED

--- Signalling of faulty data packets by red flashing of a two-colour LED

--- Connection of the Modbus cable to a lead-through termi-nal for interruption-free bus connection even with

a pulled plug-in terminal

--- Setting of a baud rate from 1200 baud to 57,600 baud via rotary coding switch

--- Setting of the Modbus module address via rotary coding switch

--- Setting of the communication parameters via DIP switch-es

--- Supported Modbus function codes: Read Input Register

--- Supported Modbus error codes: Illegal Function Code, Ille-gal Address

Dimensions 90 x 90 x 106 mm (WxHxD)

Product: SCHAKO type BKSYS-MOD

Switch cabinet BKSYS-WS1

according to degree of protection IP 66

Housing: Stable sheet steel construction consisting of 1.25 mm or 1.5 mm sheet steel, canted and welded from a single piece, with circumferential protective channel at the door opening, rear wall with countersunk bores for wall mounting support. Housing bottom with sheet steel flange plates.

All modules are completely preassembled and prewired on terminal blocks.

Maximum size: 1x GM1 + 3xEM1

Dimensions (W x H x D): 800 x 600 x 300 mm

Product: SCHAKO type BKSYS-WS1

Switch cabinet BKSYS-WS2

according to degree of protection IP 66

Housing: Stable sheet steel construction consisting of 1.25 mm or 1.5 mm sheet steel, canted and welded from a single piece, with circumferential protective channel at the door opening, rear wall with countersunk bores for wall mounting support. Housing bottom with sheet steel flange plates.

All modules are completely preassembled and prewired on terminal blocks.

Maximum size: 2x GM1 + 6xEM1

Dimensions (W x H x D): 800 x 600 x 300 mm

Product: SCHAKO type BKSYS-WS2

Transformers BKSYS- BKSYS-063 / BKSYS-160

Transformer 230 V AC / 24 V AC for power supply of the con-nected modules and spring return actuators.

63 VA:		BKSYS-063

160 VA:	BKSYS-160

Product: SCHAKO type BKSYS-063 / BKSYS-160