Active floor conventor type CNVA

Specification text

Tread-resistant high-performance floor convector model CNVA for forced convection. Consisting of a galvanised sheet steel construction with frame and grille layer made of extruded aluminium, standard anodised E6/EV1. All internal parts painted to RAL 9005, black.

2-pipe heat exchanger (standard); 4-pipe heat exchanger (optional), for cooling and heating, with frame made of galvanised sheet steel, copper pipes and aluminium ribs, suitable for water grade to VDI2035. The fan is driven by an efficient and electronically commuted EC motor (24 V DC), which is infinitely variable from 0-100% (0-10 V DC).

As standard, the floor convector SCHAKO 150/190 is equipped with a condensate pan made of stainless sheet steel painted in black. To optimise maintenance, the fan can be removed without the need for tools, and the heat exchanger can be swivelled upwards by about 45°.

The legs that are adjustable from the inside can also be adjusted from the room side in the mounting state and are fitted with decoupled fastening points for simple fastening of the convector.

As standard, all devices are provided with a stable cardboard insert during transport as protection against damage and dirt. The tread-resistant grille insert is available either as linear grille or roll-down grille as desired.

Product: SCHAKO type CNVA.

Models

Height / model H=with standard grille height without adjustable legs

--- H=106 mm B=270 mm (-106), only heating / 2-pipe

--- H=150 mm B=350 mm (-150)

--- H=190 mm B=350 mm (-190)

Model / Variant

--- 2-pipe register (-H2), cooling or heating

--- 4-pipe register (-H4), for models H=150 and H=190, cooling and heating, with condensate pan

Nominal length (NL)

--- Nominal length 1150 mm (-N1)

--- Nominal length 2000 mm (-N2)

--- Nominal length 2750 mm (-N3)

Housing position

--- Heat exchanger / register standard (-S), LG = NL

--- Heat exchanger / register centre (-M), LG>NL

--- Heat exchanger / register left (-L), LG>NL

--- Heat exchanger / register right (-R), LG>NL

Total length (LG) (*)

The total length must always be entered with 4 digits.

--- Smallest length > Nominal length

--- Greatest length = 3000 mm

Grille layer / Frame

--- Grille layer aluminium natural colour anodised E6/EV1 (-G1)

--- Grille layer aluminium black anodised E6/EV6 (-G2)

--- Grille layer aluminium bronze anodised E6/C33 (-G3)

Tread-resistant grille insert

--- Without grille insert (-00)

--- Linear grille aluminium natural colour anodised E6/EV1 (-L1)

--- Linear grille aluminium black anodised E6/EV6 (-L2)

--- Linear grille aluminium bronze anodised E6/C33 (-L3)

--- Roll-down grille aluminium natural colour anodised E6/EV1 (-R1)

--- Roll-down grille aluminium black anodised E6/EV6 (-R2)

--- Roll-down grille aluminium bronze anodised E6/C33 (-R3)

Connecting piece diameter / with or without rubber lip seal

--- Without primary air connecting piece (-P0)

--- Rectangular connecting piece only type H=106 (-P1)

--- DN 78 without rubber lip seal, only height 150 and height 190 (-P2)

--- DN 98 without rubber lip seal, only height 190 (-P3)

--- DN 123 without rubber lip seal, only height 190 (-P4)

--- DN 78 with rubber lip seal, only height 150/190 (-P5)

--- DN 98 with rubber lip seal, only height 190 (-P6)

--- DN 123 with rubber lip seal, only height 190 (-P7)

Primary air connecting piece / Position

--- Without primary air connecting piece (-0)

--- Lateral left primary air connecting piece (-1)

--- Lateral right primary air connecting piece (-2)

--- Primary air connecting piece left front side (room side) (-3)

--- Primary air connecting piece right front side (room side) (-4)

Connection position of the water connections

--- Connection position lateral left (front side) (-W1)

--- Connection position lateral right (front side) (-W2)

--- Connection position left front side (room side) (-W3)

--- Connection position right front side (room side) (-W4)

Water connections / Hydraulic connection

--- Without water connections pre-equipped ex works (-0)

--- 2-pipe valve set delivered loose, consisting of 1 straight-through valve, 1 lockshield valve with integrated pre-setting of the kv values (-1)

--- 2-pipe valve set delivered loose, consisting of 1 straight-through valve, 1 lockshield valve with integrated pre-setting of the kv values (-2)

--- With water connections pre-equipped ex works (flex) (-3)

--- With mounted straight-through valve (**), shut-off valve without actuator NL+100 mm (-4)

--- With mounted straight-through valve (**), shut-off valve and actuator thermal 24 V 2P NL+100 mm (-5)

--- With mounted straight-through valve (**), shut-off valve and actuator thermal continuously 24 V NL+100 mm (-6)

--- With mounted straight-through valve (**), shut-off valve and actuator continuously 24 V (motorised) NL+100 mm (-7)

Control

--- Electric junction box IP65 with standard electric connecting plate and spring clamps (-S0)

--- Electric junction box IP65 with electric control board and spring clamps (-S1)

End piece

--- Band design centre part without end piece (-E0)

--- Band design with right end piece (-ER)

--- Band design with left end piece(-EL)

--- Single item with 2 end pieces (-E2)

External coating

--- Housing painted on the inside and outside to RAL 9005 (-A1)

--- Housing painted on the outside rust prevention with polyester powder (-A2)

--- Housing outside with 3-mm impact sound insulation (-A3)

Adjustable legs

--- Adjustable height 70 mm (-07)

--- Adjustable height 130  mm (-13) (limited to the device dimensions in type H=106)

Protective mounting cover

--- Without protective mounting cover (-M0)

--- With cardboard insert 7-mm corrugated board (-M1)

--- With tread-resistant wooden insert (-M2)

Condensate pump

--- Without condensate pump (-K0)

--- With condensate pump delivered loose (-K1), type H=150 and H=190

--- With built-in condensate pump, only in connection with extension of the floor duct NL+200 mm, only height 150 mm and height 190 mm (-K2)

CNVAZ accessories for CNVA (at an extra charge)

Height / Model (*)

--- H=106 mm; B=270 mm  (-106)

--- H=150 mm; B=350 mm  (-150)

--- H=190 mm; B=350 mm  (-190)

Model / Variant (*)

--- Dummy piece without heat exchanger (-H0).

--- Corner piece without heat exchanger (-H5)

Angle data for corner piece / dummy element (3 digits) (*)

--- Dummy piece 180

--- Corner piece 035 to 325

Length 1 (4 digits) (*)

--- LG dummy piece 0600 – 3000 mm

--- Side length 1 for corner piece=convector width +300 mm min

--- Side length 1 for corner piece=convector width +500 mm max

Length 2 (4 digits) (*)

--- For dummy piece, enter 0000

--- Side length 1 for corner piece=convector width +300 mm min

--- Side length 1 for corner piece=convector width +500 mm max

Grille layer / Frame

--- Grille layer aluminium natural colour anodised E6/EV1 (-G1)

--- Grille layer aluminium black anodised E6/EV6 (-G2)

--- Grille layer aluminium bronze anodised E6/C33 (-G3)

Tread-resistant grille insert

--- Without grille insert (-L0)

---Linear grille aluminium natural colour anodised E6/EV1 (-L1)

--- Linear grille aluminium black anodised E6/EV6 (-L2)

--- Linear grille aluminium bronze anodised E6/C33 (-L3)

--- Roll-down grille aluminium natural colour anodised E6/EV1 (-R1)

--- Roll-down grille aluminium black anodised E6/EV6 (-R2)

--- Roll-down grille aluminium bronze anodised E6/C33 (-R3)

Connecting piece diameter / with or without rubber lip seal

--- Without primary air connecting piece (-P0)

--- Rectangular connecting piece, only type H=106 (-P1)

--- Connecting piece DN 78 without rubber lip seal, only height 150 and height 190 (-P2)

--- Connecting piece DN 98 without rubber lip seal, only height 190 (-P3)

--- Connecting piece DN 123 without rubber lip seal, only height 190 (-P4)

--- Connecting piece DN 78 with rubber lip seal, only height 150 and height 190 (-P5)

--- Connecting piece DN 98 with rubber lip seal, height 190 (-P6)

--- Connecting piece DN 123 with rubber lip seal, height 190 (-P7)

Primary air connecting piece / Position

--- Without primary air connecting piece (-0)

--- Lateral left primary air connecting piece (-1)

--- Lateral right primary air connecting piece (-2)

--- Primary air connecting piece left front side (room side) (-3)

--- Primary air connecting piece right front side (room side) (-4)

--- Primary air connecting piece centre dummy piece (-5)

--- With two primary air connecting pieces centre dummy piece (-6)

End piece

--- Band design centre part without end piece (-E0)

--- Single item with 2 end pieces (-E2)

--- Band design with right end piece (-ER)

--- Band design with left end piece(-EL)

External coating

--- Housing painted on the inside and outside to RAL 9005 (-A1)

--- Housing painted on the outside rust prevention with polyester powder (-A2)

--- Housing outside with 3-mm impact sound insulation (-A3)

Adjustable legs

--- Adjustable height 70 mm (-07)

--- Adjustable height 130  mm (-13) (limited to the device dimensions in type H=106)

Protective mounting cover

--- Without protective mounting cover (-M0)

--- With cardboard insert 7-mm corrugated board (-M1)

--- With tread-resistant wooden insert (-M2)

Cuts / Bevel cuts

--- Without cuts in dummy element (-A0)

--- With rectangular cuts in dummy element (linear grille) (-A1)

--- With rectangular cuts in dummy element (roll-down grille) (-A2)

--- With round cuts in dummy element (linear grille) (-A3)

--- With round cuts in dummy element (roll-down grille) (-A4)

--- With bevel cut in dummy element (linear grille) (-A5)

--- With bevel cut in dummy element (roll-down grille) (-A6)

Soundproofing bulkhead

--- Without soundproofing bulkhead in dummy element (-S0)

--- Soundproofing bulkhead with centre covering, 2 bulkhead sheets made of galvanised sheet steel, coated in black and a centre covering made of 2-mm aluminium plate, natural colour anodised. Bulkhead sheets mounted in duct ex works, space in-between filled with insulating material to be provided on site (-S1).