Ceiling Swirl Diffuser Model DQJ

Specification texts

Ceiling swirl diffuser type DQJ-Q-SR-Z-..., with square faceplate, circular blade pattern. Particularly suitable for installation in comfort rooms with high number of air changes, for clean rooms (in connection with particle filter boxes) and for VAV installations with variable volumetric flows (between 40-100%). Cooling and heating modes are possible. With faceplate made of sheet steel with high-quality powder coating, painted sheet steel RAL 9010 (white). With central pivoting, aerodynamic radially arranged air deflection blades in support blade profile sections made of plastic in a colour similar to RAL 9010 (white), RAL 9005 (black, standard) or aluminium painted to the RAL colour of the faceplate (subsequent adjustment of blades not possible). Each blade is adjustable from the diffuser faceplate without using any special device, without dismounting the diffuser. The blades are divided lengthwise, allowing an air throw with an even higher induction to be set (air throw "B"). Free cross-section, resistance and sound power level constant in all blade positions. With visible screw mounting (-SM). For NW 800 with concealed mounting (-VM), with motor adjustment only possible with SM mounting. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Volumetric flows in m³/h at:			35 dB(A)	40 dB(A)

-	NW 310				229		278

-	NW 400				275		335

-	NW 500				450		575

-	NW 600/625				680		820

-	NW 800				1000	1	220

Product: SCHAKO type DQJ-Q-SR-Z-...

-	for supply air, with continuous air deflection blades, square faceplate and circular blade pattern Standard with central mounting (-MM), only possible in connection with plenum box. For NW 800 with concealed mounting (-VM). TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-Q-SR-Z-...-PS-...

-	for return air, without air deflection blades, with square faceplate, circular perforation. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Volumetric flows in m³/h at:		35 dB(A)	40 dB(A)

-	NW 310				443		533

-	NW 400				498		604

-	NW 500				760		921

-	NW 600/625				1336		1536

-	NW 800				1625		1868

Product: SCHAKO type DQJ-Q-SR-A-...

-	for supply air, with air deflection blades, with square faceplate, square blade pattern, less noise and pressure loss at the same volumetric flow. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Volumetric flows in m³/h at:			35 dB(A)	40 dB(A)

-	NW 310					250		300

-	NW 400					295		350

-	NW 500					550		660

-	NW 600/625					740		900

-	NW 800					1260		1500

Product: SCHAKO type DQJ-Q-SQ-Z-...

-	for return air, without air deflection blades, with square faceplate, square perforation, less noise and pressure loss at the same volumetric flow. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Volumetric flows in m³/h at:			35 dB(A)	40 dB(A)

-	NW 310					475		570

-	NW 400					495		605

-	NW 500					810		1000

-	NW 600/625					1380		1700

-	NW 800					1770		2130

Product: SCHAKO type DQJ-Q-SQ-A-...

-	for supply air, with air deflection blades, with radial faceplate, circular blade pattern. Standard with concealed mounting    (-VM). TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-R-SR-Z-...

-	for supply air, with continuous air deflection blades, with round faceplate, circular blade pattern. Standard with central mounting (-MM), only possible in connection with plenum box. For NW 800 with concealed mounting (-VM). TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-R-SR-Z-...-PS-...

-	for return air, without air deflection blades, with round faceplate, circular perforation. Standard with concealed mounting (-VM). TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-R-SR-A-...

-	for supply air, with air deflection blades, with square faceplate and circular blade pattern. With concealed mounting (-VM, screw mounting SM not possible), double-folded edge, especially for use under the ceiling. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-S-SR-Z-...

-	for return air, with square faceplate, radial blade pattern. With concealed mounting (-VM, screw mounting -SM not possible), double-folded edge, especially for use under the ceiling. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-S-SR-A-...

-	for supply air, with continuous air deflection blades, square faceplate and circular blade pattern With concealed mounting (-VM, screw mounting -SM not possible), double-folded edge, especially for use under the ceiling. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-S-SR-Z-...-PS-...

-	for supply air, with air deflection blades, with square faceplate and circular blade pattern. With concealed mounting (-VM, screw mounting -SM not possible), double-folded edge, especially for use under the ceiling. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-S-SQ-Z-...

-	for return air, without air deflection blades, with square faceplate and square blade pattern. With concealed mounting

(-VM, screw mounting -SM not possible), double-folded edge, especially for use under the ceiling. TÜV inspected according to VDI 6022 Sheets 1+2, as well as DIN 1946 Sheet 2.

Product: SCHAKO type DQJ-S-SQ-A-...

-	with air throw pattern "A" for longer horizontal throw distance.

-	with air throw pattern "B": blades in blade positions 1+2

-	with air throw pattern "C": without blades (only possible for return air)

-	with air throw pattern "V": all blades in blade position 1 (heating mode only)

-	Faceplate made of:

-	Sheet steel painted to a different RAL colour

-	Natural colour anodised aluminium (E6/EV1) (not available for DQJ-R-... and DQJ-S-... models).

-	Stainless steel painted in the colour sand silver (not available for DQJ-S-... model)

-	Galvanised sheet steel (not available for DQJ-S-...)

-	with concealed mounting (-VM), made of aerodynamic aluminium profile with 2-point (NW 310), 4-point (up to NW 500) or 6-point suspension (from NW 600), only possible in conjunction with SK-Q-.../SK-R-..., without SK-Q-.../ SK-R-...; the counter pole brace must be provided on site)

-	with screw mounting with concealed mounting (-VS), for mounting with ball-impact guard (-BS) (only for NW 800, not possible for DQJ-S-...).

Accessories:

-	Plenum box (SK-Q-01-... and SK-R-01-...) made of galvanised sheet steel, with fixing lugs.

-	Supply air model with integrated perforated straightener.

-	Return air model inside painted to RAL 9005 (black)

-	with damper (-DK1) in plenum box, adjustable from below, for simple air volume regulation without dismounting the faceplate.

-  adjustable from below with cable (-DK2)

-	with volumetric flow meter (-VME1).

-	with ROB model (-ROB1), removable diffuser plate, damper and volumetric flow meter (only SK-Q-01-...)	-	with rubber lip seal (-GD1), at the connection spigot made of special rubber.

-	with thermal insulation

-	internal (-Ii)

-	external (-Ia)

-	Height of plenum box can be freely selected, xxx in mm (minimum height = spigot diameter + 102 mm for SK-Q-01-... and spigot diameter +137 mm for SK-R-01-..., but at least 235 mm) (For models SK-Q-01-Z-310 / -400-...-DK1 / -DK2-...-S0 and SK-R-01-Z-310 / -400 / -500-...-DK1 / -DK2-...-S0, observe special height of plenum box (see p. 12))

-	Spigot diameter can be freely selected, xxx in mm

-	Spigot position:

-	S0= spigot from above

-	S1= 1 lateral spigot on the box (standard)

-	S2= 2 spigots offset by 90°

-	S3= 2 spigots offset by 180°

-	S5= 2 spigots arranged next to each other

-	Motor adjustment (-M1 / -M2), with electric actuators (only DQJ-Q-SR-Z-...-PS-... NW 500-800 only with screw mounting) for optimum and simple change of the air throw pattern when requirements change. A damper that may have been built in has been built in offset by 90° and must be adjusted by dismounting the faceplate.

-	Galvanised sheet steel hit-and-miss damper (-SS) for air volume regulation (only for DQJ-Q/S-SR-... / DQJ-Q/S-SQ-...), particularly suitable in low-lying ducts for optimum air inflow.

-	Adjustable damper (-DV) made of galvanised sheet steel (only possible for DQJ-R-SR-... with screw mounting (-SM)).

-	1/4 cover plate (-AD), made of galvanised sheet steel for individual adaptation of the air flow to room conditions (only possible for supply air version)

-	Ball-impact guard (-BS), made of steel with high-quality powder coating in RAL 9010 (white), other RAL colours possible at an extra charge (possible only for DQJ-Q/R-SR-... / DQJ-Q-SQ-... with SM mounting and for NW 800 only with VS mounting).