Slot diffuser DSC

Specification text

Highly inductive slot diffuser, free cross-section, resistance and sound power level constant in all blade positions, suitable for use in rooms with a height between 2.6 m and 4 m.

| Volumetric flows in m³/h per m at: | 35 dB(A) | 40 dB(A) |
| --- | --- | --- |
| DSC-1 | 131 | 156 |
| DSC-2 | 203 | 242 |
| DSC-3 | 234 | 279 |
| DSC-4 | 253 | 302 |

Supply air model with pivoting air deflection blades in support profile shape made of plastic material (hard PVC):

- 	Colour similar to RAL 9005 (black, standard) (-L9005).

-	Colour similar to RAL 9006 (white aluminium) (-L9006).

-	Colour similar to RAL 9010 (white) (-L9010).

-	painted to a freely selectable RAL colour (-Lxxxx, always with 5 digits).

Product: SCHAKO type DSC-…-Z-…

Return air model without air deflection blades (-00000), with perforated plate made of sheet steel painted to RAL 9005 (black), as cover screen.

Product: SCHAKO type DSC-…-A-…

Model (number of slots):

-	1-slot (-1)

-	2-slot (-2)

-	3-slot (-3)

-	4-slot (-4)

Frame profile:

-	STANDARD frame profile (-R0)

-	narrow frame profile (-S0)

-	special frame profile (-P0)

Frame surface:

-	Natural colour anodised aluminium (standard, -ELOX)

-	Aluminium painted to:

-	RAL colour 9006 (white aluminium) (-9006)

-	RAL colour 9010 (white) (-9010)

-	a different RAL colour, freely selectable (-xxxx) (always with 4 digits).

Blade position for air jet:

-	without blades, for return air, with perforated plate (-0)

-	Blades with vertical throw (-V)

-	blades with horizontal one-way throw to the left (-L)

-	blades with horizontal one-way throw to the right (-R)

-	blades with horizontal two-way throw (-B)

-	blades with horizontal diverging throw (multi-direction throw) (standard) (-D)

Length / Model:

Single design (-N)

-	length L= 1000 mm (-N-01000)

-	length L= 1500 mm (-N-01500)

-	Length (L) in mm, freely selectable (-N-xxxxx, always with 5 digits).

(can be fitted with a plenum box in case of single design lengths L = ≥ 400 mm to ≤ 1500 mm)

Band design (-B)

-	Length (BL) in mm, as band (-B-xxxxx).

(Available lengths according to SCHAKO standard). With connecting pins, supplied loose (2 for each connection).

Mounting:

-	without connection (-00)

-	Only possible without plenum box and without hit-and-miss damper.

-	Permanent connection with plenum box (-FV)

-	Only possible with plenum box.

-	As standard for the models DSC-…-R0 / DSC-…-S0 and DSC-…-P0.

-	The slot diffuser is permanently connected to the plenum box.

-	Concealed mounting with plenum box (-VM)

-	Only possible with plenum box.

-	Possible for the models DSC-…-R0 / DSC-…-P0 and DSC-…-S0-…-Z2 (with additional profile).

-	Not possible for the models DSC-…-S0-…-Z0 / DSC-…-S0-…-Z1 / DSC-…-S0-…-Z3.

-	The slot diffuser is screwed to the pole brace in the plenum box housing with concealed screws.

-	Frame with foam gasket.

-	Plenum box supplied loose from the factory.

-	Mounting with counter pole brace (-GT)

-	Only possible without plenum box.

-	Screws and clamp straps are supplied loose (2 pieces).

-	Pole brace traps consisting of folded galvanised sheet steel and pole brace made of extruded aluminium profile with DIN thread.

-	Possible for the models DSC-...-R0 / DSC-...-P0 and DSC-...-S0-...-Z2 (with additional profile).

-	Not possible for the models DSC-...-S0-...-Z0 / DSC-...-S0-...-Z1 / DSC-…-S0-…-Z3.

-	The slot diffuser is screwed to the counter pole brace (pole brace strap) with concealed screws (included in delivery).

-	For mounting, access on the rear is required!

-	Mounting with clamp strap (-KB)

- 	Only possible without plenum box.

-	Screws and clamp straps are supplied loose (2 pieces).

-	Clamp strap made of galvanised sheet steel.

-	Possible for the models DSC-...-R0 / DSC-...-P0 and DSC-...-S0-...-Z2 (with additional profile).

-	Not possible for the models DSC-...-S0-...-Z0 / DSC-...-S0-...-Z1 / DSC-…-S0-...-Z3.

-	The slot diffuser is screwed to the clamp strap with concealed screws (included in delivery).

-	For mounting, access on the rear is not required!

-	Screw mounting (-SM)

-	Only possible without plenum box.

-- Screws must be provided on site

-	Possible for the models DSC-…-R0 and DSC-…-P0.

-	Not possible for the model DSC-…-S0.

-	The slot diffuser is fixed with visible screws.

-	Mounting with suspension lugs (-AL)

- 	Only possible without plenum box.

-	4 pieces, supplied loose.

-	Possible for the models DSC-…-R0 and DSC-…-P0.

-	Not possible for the model DSC-…-S0.

-	The slot diffuser is fastened to 4 suspension brackets

-	Suspension lug made of galvanised sheet steel, with holes for hook mounting.

Accessories:

-	End pieces (-E0 / -ES / -EB / -EL / -ER)

-	without end piece (-E0) (standard)

-	with end pieces, made of aluminium (same colour as frame):

-	supplied loose (-ES, pair) (standard)

-	mounted ex works on both sides (-EB)

-	mounted ex works on the left side (-EL)

-	mounted ex works on the right side (-ER)

-	Additional profile (-Z0 / -Z1 / -Z2 / -Z3)

-	Without additional profile (-Z0) (standard).

-	with additional profile made of aluminium (same colour as frame, only possible for DSC-…-S0):

-	Z I (-Z1): connection of ceiling panels.

-	Z II (-Z2): connection of panelled ceilings.

-	Z III (-Z3): connection of ceiling panels.

-	Dummy piece (-BS0 / -BS1)

-	without dummy piece (-BS0) (standard).

-	with dummy piece (-BS1):

-	made of sheet steel painted to RAL 9005 (black).

-	only possible without plenum box and hit-and-miss damper.

-	with fastening clips for mounting on the slot diffuser.

-	possible from length L ≥ 200 mm.

-	Mounting only possible with suspension lugs (-AL, standard in connection with active diffuser DSC-…-FV-…), counter pole brace (-GT) or clamp strap (-KB).

-	Hit-and-miss damper (-SN / -SS)

-	without hit-and-miss damper (-SN) (standard).

-	with hit-and-miss damper (-SS).

-	made of electrolytically galvanised sheet steel.

-	Only possible without plenum box.

-	Mounting:

-	DSC-…-R0 / DSC-…-P0:

-	with screw mounting (-SM, standard)

-	mounting with counter pole brace (-GT)

-	DSC-…-S0:

-	Screw mounting not possible.

-	mounting with counter pole brace (-GT)

-	Only possible for models with additional profile -Z2. Not possible for models without additional profile and models with additional profiles -Z1 and -Z3.

### - Plenum box (-ASK-24), with mounting brackets.

-	Model (number of slots):

-	1-slot (-1)

-	2-slot (-2)

-	3-slot (-3)

-	4-slot (-4)

-	Single / band design:

-	Single design (-N, length of box KL max. 1500 mm)

-	Band design (-B, available lengths according to SCHAKO standard for band design)

-	Length:

-	Length L = 1000 mm (-01000) (KL = 997 mm)

-	Length L = 1500 mm (-01500) (KL = 1497 mm)

-	Length (L/BL) in mm, freely selectable (-xxxxx, always with 5 digits)

(Length of box KL = L-3 / total length of box GKL = BL-3, can be fitted with a plenum box in case of single design lengths L = ≥ 400 mm to ≤ 1500 mm)

-	Mounting of box:

-	Permanent connection (-FV) (standard)

-	concealed mounting (-VM) (only possible for the models DSC-…-R0 / DSC-…-P0 and DSC-…-S0-…-Z2)

-	without fastening (only possible without diffuser) (-00)

-	Material:

-	Galvanised sheet steel (-SV) (standard)

-	Damper:

-	without damper (-DK0) (standard)

-	With damper made of galvanised sheet steel, adjustable, for simple air volume regulation:

-	in the plenum box housing (only with lateral spigot position [-S1/-S2]) (-DK1)

-	in the connection spigot, with cable-operated adjustment (with spigot position from above [-S0]) (-DK2)

-	Rubber lip seal:

-	without rubber lip seal (-GD0) (standard)

-	With rubber lip seal (-GD1) made of special rubber, at the connection spigot.

-	Insulation:

-	without insulation (-I0) (standard)

-	with internal insulation (-Ii), thermal insulation inside the plenum box.

-	with external insulation (-Ia), thermal insulation at the outside of the plenum box.

-	Height of plenum box:

-	standard height of plenum box (-KHS)

-	height of box in mm, freely selectable (-xxx, always with 3 digits)

(Minimum height [GH] with spigot position S1+S2 and standard box neck = spigot diameter øD + 82 mm / with spigot position S0 = 180 mm)

-	Box neck:

-	standard box neck (-KVS) (KVS = 45 mm)

-	box neck extension in mm, freely selectable (-xxx, always with 3 digits), box neck (not adjustable) from ³ 45 mm to 200 mm possible.

Can only be used with 1-slot models, 2-, 3- and 4-slot models don't have a box neck.

-	Spigot position:

-	Spigot from above (-S0)

-	Lateral spigot (-S1) (standard).

-	Lateral spigot located on the opposite side (-S2) (only possible for 1-slot models)

-	Spigot diameter:

-	standard spigot diameter (-SDS)

-	spigot diameter (D) in mm, freely selectable (-xxx, always three digits)

-	Suspension:

-	without riveting nut (-E0) (standard)

-	With riveting nut (-EM), made of brass.

-	with air diffuser plate (FQ = 46%), made of galvanised sheet steel, (only for models with spigot from above).

-	Corner angle (-EW-24), frame and dummy profile made of extruded aluminium profile. Mounting with suspension lugs (-AL), supplied loose.

-	Model (number of slots):

-	1-slot (-1)

-	2-slot (-2)

-	3-slot (-3)

-	4-slot (-4)

-	Frame profile:

-	STANDARD frame profile (-R0)

-	Narrow frame profile (-S0)

-	Special frame profile (-P0)

-	Frame surface:

-	Natural colour anodised aluminium (standard, -ELOX)

-	Aluminium painted to:

-	RAL colour 9006 (white aluminium) (-9006)

-	RAL colour 9010 (white) (-9010)

-	a freely selectable RAL colour (-xxxx, always with 4 digits)

-	Dummy profile colour:

-	Dummy profile made of painted aluminium:

-	colour similar to RAL 9005 (black) (-B9005, standard)

-	colour similar to RAL 9006 (white aluminium) (-B9006)

-	colour similar to RAL 9010 (white) (-B9010)

-	RAL colour freely selectable (-Bxxxx) (always with 5 digits)

-	Angle between sides:

-	angle  = 90° (-090) (standard)

-	angle () as required (-xxx), values between  = 90° (-090, standard) and 170° (-170) are possible (always with 3 digits).

-	Left-side length (a):

-	standard length, 1- / 2- / 3-slot L = 250 mm / 4-slot L = 400 mm (-000).

-	length (L) in mm, freely selectable (-xxx) (minimum length = standard length) (always with 3 digits).

-	Right-side length (b):

-	standard length, 1- / 2- / 3-slot L = 250 mm / 4-slot L = 400 mm (-000).

-	Length (L) in mm, freely selectable (-xxx) (minimum length = standard length) (always with 3 digits).

-	Including 4 fishplates (-VL, included in delivery) made of aluminium (same colour as frame), supplied loose.

-	Additional profile:

-	without additional profile (-Z0) (standard)