Smoke Detection System Model RMS

Specification texts

The smoke extraction blade damper ERK-MB meets the requi-rements of EN 12101-8, EN 13501-4, EN 1366-2 and EN 1366-10. The ERK MB has been inspected according to EN 1366-2 and EN 1366-10 in accordance with the Declaration of Perfor-mance No. DoP-ERK-MB-2019-04-01.

Classification according to EN 13501-4 is EI 90 (vedw, hod i↔o) S 1000 C10000 MA multi., depending on the mounting situation

Smoke extraction blade dampers for multiple sections in rectangular design are intended for extraction of smoke within smoke extraction systems to smoke and heat control systems.

Housing and blade dampers are made of abrasion-resistant, mineral silicate structural panels. The blade damper axles ma-de of stainless steel are mounted in maintenance-free bronze bushes.

The smoke extraction blade dampers are driven by a reversible OPEN/CLOSE actuator with 24 V AC/DC or 230 V AC supply vol-tage. It is located in a thermally insulated actuator housing to ensure correct opening and closing of the smoke extraction blade damper under fire conditions.

With stop bar seals to meet the cold and hot leakage require-ments.

Can be used with blade damper axle in horizontal or vertical position.

Any accessories that may be required for the respective mounting situation are listed in separate positions of the bill of quantities.

Installation

o	in solid walls (can be installed without clearance when mounted next to each other/above each other)

o	on solid smoke extraction shafts

(in connection with mounting brackets WE-S and horizon-tal blade damper axle)

o	in dry building walls

o	in, on and on the front and on the side of horizontal smo-ke extraction ducts (with additional on-site suspensions 	and connections)

o	in and on the front and on the side of vertical smoke extraction ducts (with additional on-site suspensions and 	connections)

Product: 	SCHAKO type ERK-MB

Declaration of Performance No. DoP-ERK-MB-2019-04-01

Dimensions:

Width (W): .................... mm

Height (H):	 .................... mm

Length (L):	 …………………. mm

Unless stated otherwise, the actuator EK10 (24 V AC/DC) will be delivered. Standard length L = 250 mm.

Alternative models or accessories (at an extra charge)

("Select as desired")

•	Housing and blade dampers with additional impregnation or colour coating (ex works only)

o	SR impregnation for protection against aggressive me-dia

- inside

- outside

- inside and outside

o	Impregnation 2000 for hydrophobization (protection against humidity)

- inside

- outside

- inside and outside

o	Colour coating (dispersion/alkyd resin-based paint) RAL colour must be specified when ordering

- inside

- outside

- inside and outside

•	Actuators with integrated limit switches for indication of the blade damper end positions

o		EK11 (SEL 2.90; actuator 230 V AC)

o		EK20 (BE 24; actuator 24 V AC / DC)

o		EK21 (BE 230; actuator 230 V AC)

•	Actuator with SLC technology for activating and monitoring smoke extraction blade dampers. The smoke 	extraction blade dam-per is connected only with one two-wire line by means of the SLC technology, detecting 	and reporting short-circuit or line break of the SLC lines by constant monitoring.

O	EK12 (SEL 1.90 SLC; actuator 24 V AC/DC; without

additional required communication device)

Suitable communication devices, for example SPMa1SR (part of EK14) or SPLM-4S 0SD Mod. allow retrieving 	data, such as indication of end position, keeping timeframe (<60 s) or tor-que monitoring. The function of the 	actuator EK12 is only ac-tive when an additional required communication device is connected.

o	EK14 (EK12; actuator 24 V AC/DC;

including communication device SPMa-1SR)

Security grille type ASG-E, made of galvanised sheet steel, mesh width ≤ 20 mm. Already mounted ex works on one side on the operating side BS (standard).

o	ASG3 = mounted ex works on both sides

o	ASG4 = 1 piece loose

Product: 	SCHAKO type ASG-E

Dimensions:

Width (W):	..................... mm

Height (H): 	..................... mm

Profile connection frame type PAR, made of galvanised sheet steel, for connecting flexible spigot type FS-E, security grilles ASG-E or inspected sheet steel ducts.

o	PAR1 = mounted ex works on operating side BS

o	PAR2 = mounted ex works on wall side MS

o	PAR3 = mounted ex works on both sides

o	PAR4 = 1 piece loose

o	PAR5 = 2 pieces loose

Product: 	SCHAKO type PAR

Dimensions:

Width (W):	 .................... mm

Height (H):	 .................... mm

Flexible spigot type FS-E, in accordance with EN 12101-7, tested according to EN 1366-9; with flange strengthener and screw bolt. Temperature-resistant up to 600°C. Expansion com-pensation at least 100 mm when mounted. The smoke extrac-tion blade damper must not be subject to mechanical stress under any circumstances. For connection to smoke extraction duct made of sheet steel. Profile connection frame PAR is re-quired for mounting.

o	PFS1 = PAR mounted ex works on operating side BS + FS-E loo-se

o	PFS2 = PAR mounted ex works on wall side MS + FS-E loose

o	PFS3 = PAR mounted ex works on both sides + FS-E (2 pieces) loose

o	PFS4 = PAR + FS-E (1 pieces each) loose

o	PFS5 = PAR + FS-E (2 pieces each) loose

Product: 	SCHAKO type FS-E

Dimensions:

Width (W):   	 .................... mm

Height (H):	 .................... mm

Mounting bracket type WE-S, made of galvanised sheet steel, dimensions 100 x 100 x 160 mm. Required for installation on solid smoke extraction shafts made, for example of concrete. The exact arrangement and number of mounting brackets WE-S must be selected according to the ERK-MB-V dimensions, see

Table 3 and Table 4 on page 13.

Product: 	SCHAKO Mounting bracket type WE-S

Dimensions (W/H according to the dimensions of the smoke extraction blade damper)

Width (W): .................... mm

Height (H):	 .................... mm

The mounting brackets WE-S are delivered only if they have been explicitly ordered and according to specifications for the mounting situation.