Particle filter box FKW

Specification texts

Particle filter box with safely sealing pressure device and sealing device for installation of filter cells with rubber seal. With vertical, round connection spigot. With integrated differential pressure/aerosol test device with measuring spigot inside the box, for hose connection with an outer diameter of 10 mm (-D1).

Without shut-off damper and without seal leakage test.

Make: SCHAKO type FKW-H-...-M000-D1-...-P0-...

-	with vertical, round connection spigot and manually adjustable sealing shut-off damper. Leakage at closed damper blade according to DIN EN 1751, class 4, at a duct pressure of up to 1000 Pa. Without seal leakage test.

With integrated differential pressure/aerosol test device with measuring spigot inside the box, for hose connection with an outer diameter of 10 mm (-D1). Without seal leakage test.

Make: SCHAKO type FKW-H-...-M001-D1-...-P0-...

-	with vertical, round connection spigot and electrically (OPEN/CLOSED actuator) adjustable locking shut-off damper (with/without spring return).

Leakage at closed damper blade according to DIN EN 1751, class 4, at a duct pressure of up to 1000 Pa.

With integrated differential pressure/aerosol test device with measuring spigot inside the box, for hose connection with an outer diameter of 10 mm (-D1). Without seal leakage test.

Make: SCHAKO type FKW-H-...-Exxx-D1-...-P0-...

-	with horizontal, round connection spigot. With integrated differential pressure/aerosol test device with measuring spigot inside the box, for hose connection with an outer diameter of 10 mm (-D1). Without shut-off damper and without seal leakage test.

Make: SCHAKO type FKW-V-...-M000-D1-...-P0-...

-	with horizontal, round connection spigot and manually adjustable sealing shut-off damper. Leakage at closed damper blade according to DIN EN 1751, class 4, at a duct pressure of up to 1000 Pa.

With integrated differential pressure/aerosol test device with measuring spigot inside the box, for hose connection with an outer diameter of 10 mm (-D1). Without seal leakage test.

Make: SCHAKO type FKW-V-...-M001-D1-...-P0-...

-	with vertical, rectangular connection spigot, with connection flange. With integrated differential pressure/aerosol test device with measuring spigot inside the box, for hose connection with an outer diameter of 10 mm (-D1). Without shut-off damper and without seal leakage test.

Make: SCHAKO type FKW-Q-...-M000-D1-...-P0-...

Filter height:

-	90 mm (-1)

-	150 mm (-2)

Material:

-	Filter box made of electrolytically galvanised sheet steel (-SB) (standard)

-	painted inside and outside, RAL colour white (-9010) (standard)

-	painted inside and outside, RAL colour can be freely selected (-xxxx)

-	Filter box made of stainless steel V2A (-V2-0000)

Antibacterial coating:

-	Without antibacterial coating (-AB0, standard)

-	with antibacterial coating (-AB1)

Mounting:

-	with magnetic fastening (-MB) (only available as -SB model, only available for air diffuser FDBB-...-SB [standard])

-	Concealed mounting (-VM) (standard for FDBB-...-V2 and FDBB-...-AL).

Box dimensions:

-	Standard depth of the plenum box (-KHS [for dimensions T / T1 / T2])

-	Depth of plenum box in mm (-xxx, always with 3 digits) (minimum depth = for FKW-1-... spigot diameter + 222 mm, for FKW-2-... spigot diameter + 282 mm)

Spigot diameter:

-	Standard spigot diameter (-SDS)

-	Spigot diameter ............... mm (-xxx, always with 3 digits)

(for spigot diameter > than standard only possible with box of a larger depth, maximum depth of box = 580 mm)

Diffusers (for supply air and return air):

-	Air diffuser FDBB-... (-74)

Accessories (at an extra charge):

-	Seal leakage monitoring system (-P1)

-	inside the box, only possible for particle filter with U-profile seal (-D).

-	Differential pressure / aerosol monitoring device

-	With measuring spigot inside the box, for hose connection with an outer diameter of 10 mm. Additionally with 2 measuring spigots on the box outside, for a hose with an inner diameter of 4 mm (-D2).

-	With measuring spigot inside the box, for hose connection with an outer diameter of 10 mm. Additionally with 2 measuring spigots on the box outside, for a hose with an inner diameter of 4 mm and aerosol feeding device in the spigot of the box inside (-D3).

-	With measuring spigot inside the box, for hose connection with an outer diameter of 10 mm. Additionally with aerosol feeding device in the spigot of the box inside (-D4).

-	With measuring spigot inside the box, for hose connection with an outer diameter of 10 mm. Additionally with aerosol feeding device in the spigot on the outside (-D5).

-	Differential pressure transducer (-U1)

-	only available in connection with differential pressure/aerosol monitoring devices -D2 and -D3.

-	supplied loose or optionally mounted to box outside

-	Rubber lip seal (-GD1),

-	made of special rubber (only available for FKW-...-H / -V)

-	Particle filter

-	Filter frame H=90 mm

-	UXS (-2) made of MDF wood.

Without handle cover (-G0, standard) or with double-sided handle protection (-G1, at an extra charge).

-	UXA (-3), made of aluminium.

With double-sided handle protection (-G1).

-	Rubber seal on filter housing either with continuous seal (-E, standard), U-profile seal (-D) or flat seal (-F). 	-	Filter classes HEPA H13 (-H13, >99.95%) / HEPA H14       (-H14, >99.995%).

-	Filter checked by means of oil thread test (-O, standard) or scan test (-S, at an extra charge) according to DIN EN 1822.

-	Temperature-resistant up to 80°C. Filter wrapped in film

Specification texts for air diffusers

(for supply air and return air)

Air diffuser FDBB (-74)

Air diffuser FDBB-... for supply and return air, rectangular design, free cross-section, resistance and noise level remain constant in all blade positions. Consisting of faceplate in model A (one- or two-way throw), with pivoting air deflection blades individually adjustable. Model in single length.

Dimension: 625 x 315 (length x height)

Product: SCHAKO type FDBB-A-...-625-315-N-...

-	Air throw:

-	Supply air: one-way throw (-Z1)

-	Supply air: two-way throw (-Z2)

-	Return air, without blades (-AA)

-	Return air, with blades (-AB)

-	Faceplate made of:

-	Sheet steel (-SB)

-	only available with paint

-	Painted to the RAL colour 9010 (white) (-9010)

-	painted, RAL colour can be freely selected (-xxxx)

-	Stainless steel (V2A) painted in sand silver

-	Natural colour anodised aluminium (-AL-ELOX)

(only possible with concealed mounting)

-	Stainless steel 1.4301 (V2A) (-V2-0000)

-	Blade colour

-	without blades (standard for return air) (-00000)

-	Blades made of plastic, similar to RAL colour 9005 (black, standard) (-L9005)

-	Blades made of plastic, similar to RAL colour 9010 (white, standard) (-L9010)

-	Blades made of aluminium painted to the RAL colour of the faceplate (always with 5 digits), subsequent adjustment not possible (-Axxxx)

-	Blades made of natural colour anodised aluminium (-AELOX)

-	Mounting:

-	Magnetic fastening (-MB), with safety cable.

-	Standard for sheet steel model (-SB). Not possible for aluminium (-AL and -V2 not possible) and stainless steel (-V2) models. Installation only possible in front of the wall.

-	Concealed mounting (-VM)

-	Standard for model made of aluminium (-AL) and stainless steel (-V2)

-	Pole brace fastening, by means of two M6 cylinder screws

(according to DIN EN ISO 4762) to the particle filter box.

-	Antibacterial coating:

-	Without antibacterial coating (-AB0, standard)

-	with antibacterial coating (-AB1)