Multi-Leaf Damper Model HK

Specification texts

Multi-leaf damper, consisting of dimensionally stable profiled frame made of 1.5 mm galvanised sheet steel, frame depth 180 mm with profiled connection frame (4-screw duct connection), with joint flow-favouring hollow-body blades adjustable in opposite directions made of profiled galvanised sheet steel. Suitable for pressures up to 1000 Pa.

The blades are adjusted via external, actuating lever, actuator/servo cylinder.

Housing leakage according to DIN EN 1751, class B, at a duct pressure of up to 1000 Pa.

-	with plastic bearing, temperature-resistant up to +80°C.

Frame depth 180 mm. Manually adjustable. Locking device (hand lever and console) supplied loose.

Product: SCHAKO type HK-P

-	With sintered bearing, temperature resistant up to +100°C.

Frame depth 180 mm. Manually adjustable. Locking device (hand lever and console) supplied loose.

Product: SCHAKO type HK-U

-	with brass bearing, temperature-resistant up to +120°C. Frame depth 180 mm. Damper leaf made of galvanised sheet steel (only H = 100 combined with W = 201-400 available).

Manually adjustable. Locking device (hand lever and console) mounted ex works.

Product: SCHAKO type HK-K

-	Frame and hollow-body blades made of stainless steel 1.4301 (V2A) (HK-K not possible).

-	with frame bore

-	on one side (RB1)

-	on two sides (-RB2)

Accessories:

-	Add-on parts

-	Installation frame (-ER2), 35/35/4 with riveted wall anchors

-	Flat-steel counter frame (-FG1), 33/5

-	Angular steel counter frame (-WG1), 30/30/3

-	Locking device (-M001, not for HK-K), console and hand lever mounted ex works to the multi-leaf damper.

-	Shaft design (W01= 50 mm, W02= 100 mm, W03= 150 mm)

-	with electric actuator

-	  5 Nm, 24 V AC/DC (-E001) / 230 V AC (-E002)

-	10 Nm, 24 V AC/DC (-E003) / 230 V AC (-E004)

-	20 Nm, 24 V AC/DC (-E005) / 230 V AC (-E006)

-	40 Nm, 24 V AC/DC (-E015) / 230 V AC (-E008)

-	5 Nm, 0 - 10 V DC, 24 V AC/DC (-E012) / 230 V AC (-E016)

-	10 Nm, 0 - 10 V DC, 24 V AC/DC (-E013) / 230 V AC (-E017)

-	20 Nm, 0 - 10 V DC, 24 V AC/DC (-E014) / 230 V AC (-E018)

-	Spring return actuator 4 Nm, 24 V AC/DC (-E021, -E023)

-	Spring return actuator 10 Nm, 24 V AC/DC (-E027, -E028)

-	Spring return actuator 20 Nm, 24 V AC/DC (-E025, -E026)

-	Spring return actuator 4 Nm, 230 V AC (-E020)

-	Spring return actuator 10 Nm, 230 V AC (-E029)

-	Spring return actuator 20 Nm, 230 V AC (-E024)

-	limit switch

-	"CLOSED" (-ESZ)

-	"OPEN" (-ESA)

-	with 2 limit switches, "CLOSED" and "OPEN" (-ES2)

-	with pneumatic servo cylinder (not for HK-K)

-	Piston force 295 N  (supply) / 247 N (return), 6 bar, double-acting (-P001)

-	Piston force 753 N  (supply) / 633 N (return), 6 bar, double-acting (-P002)

-	including bearing block