Air diffuser for open ceiling systems LOD

Specification Text

The SCHAKO air diffuser LOD for open ceiling systems has been developed for use in supply and return air systems.

The air diffuser is suitable for direct connection to the duct system and is suitable for VAV systems with variable volumetric flows of 40-100%.

The air diffuser is placed directly above the open ceiling system under the raw ceiling. It can be mounted directly against the solid ceiling (acoustic decoupling on site), or suspended. Height and design have been adapted to open ceiling systems. In cooling mode as well as in heating mode, a very high induction (I=30.2 at 80 m³/h at a distance of 2 m and a temperature difference of 8 K) is achieved after blowing out the supply air, which effectively reduces the air velocity and temperature above the open ceiling system. The supply air above the open ceiling system flows out evenly and sinks into the occupied area at a very low velocity.

The air diffuser LOD consists of a plenum box with several individual air diffusers (for supply air or return air) for the optimum discharge of supply air in cooling and heating mode, as well as a uniform suction of return air from the room. Flexible air pattern adjustment and air flow direction are optionally configurable.

The plenum box made of painted sheet steel consists of a housing with connection spigot, either round or rectangular (with flange, standard). With integrated air diffuser plate made of perforated sheet steel (only for supply air model). According to VDI 6022, the plenum box can be accessed via an inspection opening on the box bottom side. Sound power level LWA = 30 dB(A) at approx. 300 m³/h (for LOD-100-Z-5-Q-…).

-	for supply air. With round air diffuser consisting of fastening ring, cover plate and connection spigot made of painted sheet steel. With nozzle head with radially arranged apertures and integrated adjusting disc. With 3 x plugs for shielding (steering) of air jet. Plastic parts made of polystyrene (4754).

Product: SCHAKO type LOD-...-Z-...

-	for return air. With rectangular air diffuser, consisting of a frame with facing horizontal and pivoting air deflection blades of painted sheet steel (only NW 100 available).

Product: SCHAKO type LOD-...-A-...

Nominal size:

-	NW 100 (-100)

-	NW 150 (-150) (not possible for return air)

Number of air diffusers:

-	with 3 air diffusers (-3) (standard)

-	with 5 air diffusers (-5) (not possible for return air)

Connection:

-	rectangular connection (-Q) (standard)

-	round connection (-R) (NW150 for supply air with 5 air diffusers not available [LOD-150-Z-5-...])

Paint of air diffuser:

-	Sheet metal parts painted to RAL colour 9005 (black) / plastic parts similar to RAL colour 9005 (black, only for supply air) (-9005) (standard).

-	Sheet metal parts painted to RAL colour 9010 (white) / plastic parts similar to RAL colour 9010 (white, only for supply air) (-9010).

-	Sheet metal parts painted to a RAL colour of your choice, freely selectable / plastic parts similar to RAL colour 9005 (black, only for supply air) (-xxxx, always with 4 digits).

Paint of plenum box:

-	painted to RAL colour 9005 (black) (-9005) (standard).

-	painted to the colour RAL 9010 (white) (-9010).

-	painted to a RAL colour of your choice, freely selectable, (-xxxx) (always with 4 digits).

Accessories:

--	Rubber lip seal

-	without rubber lip seal (-GD0) (standard).

(Model with rectangular connection [-Q] only possible without rubber lip seal).

-	with rubber lip seal (-GD1), made of special rubber, at the connection spigot (only possible for round connection [-R]).