Mechanical Mixing Box MBM

Specification text

Mixing box for use in twin-duct air-conditioning systems, including two round connection pieces arranged at an angle of 120°, relative to one another, with control dampers with damper leaf seal made of PUR, fits ducts to DIN 24 145, sealing airtight to DIN 1946 Part 4. Fitted with integrated mechanical constant volumetric flow controller type VRM in round design, in which the mechanics and damper are in a closed control unit outside the air flow, insensitive to contamination. Differential pressure range 250 to 1,000 Pa, volumetric flow deviation ±5 %, relative to the Vmax volume. Galvanised sheet steel housing with integrated silencer unit with thermal and acoustic mineral wool lining, abrasion-resistant up to an air velocity of 20 m/s. Control damper and damper axis of sizes 100 and 125 mm are made of plastic, otherwise made of galvanised sheet steel.  Regulation of cold/hot air damper continuous or via 3-point signal, supply voltage 24V AC, 50/60 Hz, ambient temperature 0-55°C.

Product: SCHAKO type MBM

Accessories (at an extra charge)

-	Acoustic cladding (-DS) made of sound-damping mineral wool thickness 40 mm, with sheet

metal casing made of galvanised sheet steel

-	Duct silencer (-RS), outer casing and perforated sheet made of galvanised sheet steel with

mineral wool filling.

- Rubber lip seal (-GD), made of silicone-free rubber.