Mechanical Mixing Box Model MBM

Specification text

Dual duct terminal box for use in twin-duct air-conditioning systems, including two round connection spigots arranged at an angle of 120°, relative to one another, with control flaps with damper leaf seal made of PUR, fits ducts according to DIN EN 1506, sealing airtight to DIN EN 1751, class 3. Fitted with integrated mechanical constant volumetric flow controller type VM-PRO in round design, in which the mechanics and damper are in a closed control unit outside the air flow, insensitive to contamination. Differential pressure range from 250 to 1,000 Pa, volumetric flow deviation ±5 %, relative to the Vmax volume. Galvanised sheet steel housing with integrated silencer unit with thermal and acoustic mineral wool lining, abrasion-resistant up to an air velocity of 20 m/s. With nominal widths 100 und 125 mm, the control damper and damper axis are made of galvanised sheet steel. Regulation of cold/hot air damper continuously or via 3-point signal, supply voltage 24V AC, 50/60 Hz, ambient temperature 0-55°C.

Product: SCHAKO type MBM

Accessories (at an extra charge)

-	Acoustic cladding (-DS) made of sound-damping mineral wool thickness 40 mm, with sheet metal casing made of galvanised sheet steel

-	Duct silencer (-RS), outer casing and perforated sheet made of galvanised sheet steel with mineral wool filling.

-	Rubber lip seal (-GD), made of silicone-free special rubber.