Multi-Leaf damper NRWG

Specification texts

NRWG-180

NRWG multi-leaf damper, housing leakage class C and leakage with closed damper leaf class 3 to DIN EN 1751, consisting of a dimensionally stable profiled frame made of 1,5 mm galvanised sheet steel, frame depth 180 mm with joint flow-favouring hollow-body blades adjustable in oppo-site directions made of torsion-resistant aluminium profile.

The blades are adjusted by means of external plastic gear wheels arranged on one side.

- with sintered bearing

- TÜV inspected according to VDI 6022 Sheets 1+2 and DIN EN1751

- With mounting plate for flush-mounted installation in wall and ceiling²

Electric actuator with spring return (currentless OPEN)

- 20 Nm, 230 V AC, 2/3-point (-E024)

- 20 Nm, 24 V AC/DC, 2/3-point (-E025)

- 20 Nm, 24 V AC/DC, 0-10 V DC with RJ45 plug(-E072)

- 20 Nm, 24 V AC/DC, 0-10 V DC (-E073)

Electric actuator with integrated limit switches

- 2 limit switches, CLOSED and OPEN (-IS2)

Direct-current actuator

- 10 Nm, 24 V DC (-E070)

- 10 Nm, 24 V DC with RJ45 plug (-E071)

Accessories:

- Wall anchor package 1 (-M1)

- Weather protection hood (-WSH)

- Flat-roof plinth (-FLDS)

- Roof hood (-D) / Louvre hood (-L)

Tested and certified to DIN EN 12101-2 in at least the follo-wing model:

- Re1000

- SL0

- T(00)

- WL1500

- B300

- Type B with double function

Product: 				SCHAKO type NRWG-180

Nominal size:			………….  x  ……….. mm,

Aa =……………….… m²

Empty space in the building shell:	………….  x  ……….. mm

Installation position:		wall / ceiling²

2) Weather protection must be taken into account

NRWG-190

NRWG multi-leaf damper, housing leakage class C and leakage with closed damper leaf class 3 to DIN EN 1751, consisting of a dimensionally stable profiled frame made of 1,5 mm galvanised sheet steel, frame depth 190 mm with joint flow-favouring hollow-body blades adjustable in oppo-site directions made of torsion-resistant aluminium profile.

The blades are adjusted by means of external plastic gear wheels arranged on one side.

- with sintered bearing

- TÜV inspected according to VDI 6022 Sheets 1+2 and DIN EN 1751

- For mounting on wall and ceiling³ (surface mounting)

Electric actuator with spring return (currentless OPEN)

- 20 Nm, 230 V AC, 2/3-point (-E024)

- 20 Nm, 24 V AC/DC, 2/3-point (-E025)

- 20 Nm, 24 V AC/DC, 0-10 V DC with RJ45 plug(-E072)

- 20 Nm, 24 V AC/DC, 0-10 V DC (-E073)

Electric actuator with integrated limit switches

- 2 limit switches, CLOSED and OPEN (-IS2)

Direct-current actuator

- 10 Nm, 24 V DC (-E070)

- 10 Nm, 24 V DC with RJ45 plug (-E071)

Accessories:

- Wall anchor package 2 (-M2)

- Wall anchor package 3 (-M3)

- Support sheet (-AB1)

- Installation frame edge mounting (-ER1 / -ER2)

- Installation frame corner mounting (-ER3 / -ER4)

- Weather protection hood (-WSH)

- Flat-roof plinth (-FLDS)

- Roof-hood (-D) / Louvre hood (-L)

Tested and certified to DIN EN 12101-2 in at least the follo-wing model:

- Re1000

- SL0

- T(00)

- WL1500

- B300

- Type B with double function

Product: 				SCHAKO type NRWG-190

Nominal size:			………….  x  ………..  mm,

Aa = ……………….… m²

Empty space in the building shell:	………….  x  ………... mm

Installation position:		wall / ceiling²

2) Weather protection must be taken into account