Sound-Damped Volumetric Flow Controller Model Piano / Piano-S

Specification text

Sound-damped volumetric flow controller for use in supply and return air systems, for duct connection to DIN 24190, with integrated volumetric flow controller for use in constant or variable volumetric flow, room or duct pressure regulation. With positive control Vmin, Vmax or "CLOSED".

Allowed ambient temperatures: 0 - 55°C. It is possible to subsequently adjust the manufacturer-set operating volumetric flow at any time. The actual throughput of the volumetric flow can be measured via the U5 signal. The output signal can be used for master/slave or parallel operation of several controllers or for actual value display 2-10 V DC (0-10 V DC), which corresponds to 0-100 % of the set Vmax in DDC/ZLT systems.

Standard production of the galvanised sheet steel housing with mineral wool lining, with joint, opposed adjustable, flow-favouring louvres made of distortion-resistant aluminium profile and sealing rubber free of silicone for airtight design to DIN EN 1751, Class 3, with measuring cross blades made of extruded aluminium profile, blade mount made of plastic (PA6). A special measuring cross allows position-independent mounting.

-	For use in supply air systems, with electric controller, control voltage 24 V AC, 50 / 60 Hz, temperature compensation of 10-40°C, wired and adjusted in-factory.

Make: SCHAKO type Piano-E-Z or type Piano-S-E-Z with a longer silencer unit.

-	For use in return air systems, with electric controller, control voltage 24 V AC, 50 / 60 Hz, temperature compensation of 10-40°C, wired and adjusted in-factory.

Make: SCHAKO type Piano-E-A or type Piano-S-E-A with a longer silencer unit.

-	with spring return actuator (at an extra charge)

-	currentless "CLOSED"

-	currentless "OPEN"

-	For use in supply air systems, with pneumatic controller, feed pressure 1.3 bar +/- 0.1 bar, control pressure 0.1 - 1.0 bar

-	Depressurised "CLOSED"

-	Depressurised "OPEN"

Make: SCHAKO type Piano-P-Z or type Piano-S-P-Z with a longer silencer unit.

-	For use in return air systems, with pneumatic controller

Make: SCHAKO type Piano-P-A or type Piano-S-P-A with a longer silencer unit.

-	Connection: standard design with rectangular duct connection on both sides

-	Right-hand model (-R)

-	Left-hand model (-L)

Accessories (at an extra charge):

-	Flat-bed acoustic cladding (-FDS), for reducing the radiated noise, made of sound-absorbing material arranged inside the housing, thus same outer dimensions.

-	Heating register (-H2/-H4): with connection via an external thread, operating pressure 8 bar, test pressure 16 bar, consisting of galvanised sheet steel frame, copper pipes, steel collector, aluminium blades.

-	with 2 duct rows (-H2)

-	with 4 duct rows (-H4)

-	Rubber lip seal (GD) made of special rubber (for Piano or Piano-S with transition piece (ÜS) to round ducts only)

-	with DD coating (-DD) for aggressive return air

-	Transition piece, high-pressure side, made of galvanised sheet steel

-	for connection to round ducts (-ÜS)

-	for connection to rectangular ducts (-ÜSE)