Dispacement Diffuser QA

Specification texts

Displacement air diffuser is ideal for industrial plants and laboratories which produce huge amounts of hazardous substances.

The supply air enters the room at a low velocity with a temperature difference of max -4 K in the cooling mode. The contaminated air is displaced by the low induction air flow. If the displacement air diffusers are used at floor level, the supply air spreads out across the floor and is directed upwards by the convection flow from heat sources.

The return air should ideally be at high level when using displacement air diffusers. Make sure to distribute the displacement air diffusers evenly over the whole floor surface area to ensure effective floor flushing.

Especially in the presence of hazardous substances of high specific gravity, the displacement air diffuser can also be used in the occupied zone at a height of 3-4 metres. In these cases, the return air should be evacuated at floor level to about 50%.

The housing consists of base plate, round connection spigot and removable faceplate (perforated plate) for easy cleaning according to VDI 6022. To achieve even air distribution, a removable synthetic fibre filter mat is installed.

-	Type QA-V, Quarter cylinder, 90° throw,

for corner installation.

Product: SCHAKO type QA-V

-	Type QA-H, Half cylinder, 180° throw,

for installation on walls or columns.

Product: SCHAKO type QA-H

-	Type QA-R, Cylinder, 360° throw,

for mid-room installation.

Product: SCHAKO type QA-R

Material and paint (housing):

-	Galvanised sheet steel, without paint (-SV-0000) (standard).

-	sheet steel painted to RAL colour 9010 (white) (-SB-9010).

-	sheet steel painted to a different RAL colour, freely selectable (-SB-xxxx).

-	Stainless steel 1.4301 painted in the colour sand silver (-V2-SAND).

Accessories:

--	Rubber lip seal:

-	without rubber lip seal (-GD0) (standard).

-	with rubber lip seal (-GD1) made of special rubber, at the connection spigot.

--	Damper:

-	without damper (-DV0) (standard).

-	with adjustable damper (-DV1), connection without rubber lip seal, for air volume regulation, with side adjustment lever, made of the same material and painted to the same colour as the base plate / connection spigot.