Smoke Detection System Model RMS

Specification texts

Smoke detection system type RMS, with annual maintenance, for installation flush with the duct or fire

damper installation with assembly part type EBT (extra charge), with maintenance cover. Consisting of a

housing, base, cover plate, similar to RAL 9010 (white), a mounting frame made of sheet steel with seal and

with connecting cable 2.0 m long with Sub-D 9-pin connection. For use on fire and smoke dampers, with

electric or pneumatic release devices working by the zero-current closed / depressurised closed functional

principle, and with magnetic clamp and lifting magnet.

Two sensors self-monitoring permanently for correct functioning measure the air contamination due to

smoke with a special scattered light procedure outside the housing, without using a detection chamber. They

measure the degree of contamination at two points on the surface of the safety glass. Alarm and fault

messages each take place via a potential free change-over contact. Manual triggering of the smoke detector

possible via a reset button (at an extra charge).

Fastening with screw mounting (SM) (with thumb nuts or Parker screws).

Includes relay module (-RM) for supplying power and for alarm transmission incl. test switch and reset button

- with transformer for connection to 230 V AC, 50 Hz or Connection 24 V DC.

Product: SCHAKO type RMS

Accessories:

-	Assembly part (-EBT) for simple duct installation in front of the fire damper. Consisting of galvanised sheet steel with connection flanges. Housing leakage according to DIN EN 1751, class B, at a duct pressure of up to 1000 Pa

-	Assembly part (-REBT / -REBTF) for simple installation in round ducts in front of the fire damper. Consisting of galvanised sheet steel. Housing leakage according to DIN EN 1751, class B, at a duct pressure of up to 1000 Pa.

-	without flange (-REBT), with rubber lip seal made of special rubber.

-	with flange (-REBTF), on both sides, to EN 12220.