Round Duct System RR-Complete

Specification text VRA-RR

VRARR

Volumetric flow controller VRARR for the round duct system RR-COMPLETE, with electrically adjustable round damper with integrated acoustic cladding, for spiral duct connection. For use in supply/return air systems for constant or variable volume flow, room or duct pressure control. With positive control Vmin, Vmax or "CLOSED". Allowed pressure difference range: 50-1000 Pa, allowed ambient temperature 0-55°C. Suitable for use with duct velocities of 2-12 m/s. It is possible to subsequently adjust the operating volumetric flows set ex works. The output signal can be used for master/slave or parallel operation of several controllers or for actual value display 2-10 V DC (0-10 V DC), which corresponds to 0-100 % of the set Vmax in DDC/ZLT systems.

Housing consisting of 1.0 to 1.5 mm-strong outer tube, optionally with rubber seal lip made of EPDM and inner tube. With integrated acoustic cladding with mineral wool filling to DIN 4102 A2 (non-flammable). With cover on both ends. Silicone-free damper blade seal made of PUR for airtight sealing (design to DIN EN 1751). Measuring cross made of extruded aluminium profile, measuring cross support made of plastic (PA6), damper bearing made of brass. Inner tube and damper blade made of galvanised sheet steel. With electric controller, control voltage 24 V AC, 50 / 60 Hz, temperature compensation 10-40 °C, wired and adjusted in factory. TÜV inspected according to VDI 6022 Sheets 1+2.

Product: SCHAKO type VRARR

-	Housing leakage according to DIN EN 1751, class B, at a duct pressure of up to 1000 Pa.

-  Leakage with closed damper blade according to DIN EN 1751

Class 3 at a duct pressure of up to 1000 Pa.

Higher requirements upon request.

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Material and paint (housing) [outer tube / end cover]) made of:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Attachment assembly:

-	With electric actuator.

-	A001 (standard)

-	A140

-	A141

-	A160

-	A163

Alternative attachment assemblies are available upon request.

For controller selection (attachment assembly), see Controller selection on page 9.

-	Mode:

-	0-10 V (-0).

-	2-10 V (standard) (-2).

-	Volumetric flow Vmin/con :

-	ex-works, according to table (standard) (-0000).

-	4-digit value in m³/h (-xxxx).

-	Volumetric flow Vmax :

-	ex-works, according to table (standard) (-0000).

-	4-digit value in m³/h (-xxxx).

-	Damper position:

-	No spring return (standard) (-NA).

-	Currentless OPEN - normally open (-NO).

-	Currentless CLOSED - normally closed (-NC).

-	Mounting position (controller position):

-	Controller on the right-hand side, 3 o'clock (standard) (-3U).

-	Controller at the bottom, 6 o'clock (-6U).

-	Controller on the left-hand side, 9 o'clock (-9U).

-	Controller at the top 12 o'clock (-0U).

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8

threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Rubber lip seal (duct connection):

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

DKARR

Volumetric flow restrictor DKARR, for the round duct system RR-COMPLETE, with manually adjustable round damper with integrated acoustic cladding, for spiral duct connection. For use in supply and return air systems, for constant or variable volumetric flows. Allowed differential pressure range: 50-1000 Pa. Allowed ambient temperatures: 0 - 55°C

Housing consisting of 1.0 to 1.5 mm-strong outer tube, optionally with rubber seal lip made of EPDM and inner tube. With integrated acoustic cladding with mineral wool filling to DIN 4102 A2 (non-flammable). With cover on both ends. Silicone-free damper blade seal made of PUR for airtight sealing (design to DIN EN 1751). Inner tube, damper blade and manual adjusting device made of galvanised sheet steel. Measuring cross made of extruded aluminium profile, measuring cross support made of plastic (PA6), damper bearing made of brass.

Product: SCHAKO type DKARR

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Material and paint (housing) [outer tube / end cover]) made of:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Mounting position (manual adjustment position, in the air flow direction):

-	Manual adjustment on the right-hand side, 3 o'clock (standard) (-3U).

-	Manual adjustment at the bottom, 6 o'clock (-6U).

-	Manual adjustment on the left-hand side, 9 o'clock (-9U).

-	Manual adjustment at the top, 12 o'clock (-0U).

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8 threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Rubber lip seal

-	Without rubber lip seal (-GD0).

-	with rubber lip seal (-GD1), on both sides, made of EPDM

RSRR

Duct silencer RSRR, for the round duct system RR-COMPLETE. With sound absorption according to the absorption principle, by means of an annular chamber filled with mineral wool according to DIN 4102 A2 non-flammable.

Housing consisting of 1.0 to 1.5 mm-strong outer tub, optionally with rubber seal lip made of EPDM and inner tube made of perforated sheet covered abrasion-resistant toward the air flow direction. Inner tube made of galvanised sheet steel. With integrated acoustic cladding with mineral wool filling to DIN 4102 A2 (non-flammable). With end cover on both sides.

Product: SCHAKO type RSRR

-	Length:

-   1-part:

- / 750 mm / 1000 mm (-0500 / -0750 / -1000).

-   2-part:

1500 mm / 1750 mm / 2000 mm (-1500 / -1750 / -2000).

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Material and paint (housing) [outer tube / end cover]) made of:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8

threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Rubber lip seal

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

DBBRR

Round duct blade diffuser DBBRR-Z-..., for supply air, suitable for connection to DIN ducts. With integrated, manually adjustable air deflection blades. Sound power level and pressure loss remain constant in all blade positions.

Product: SCHAKO type DBBRR-Z-...

-   for return air, without air deflection blades

Product: SCHAKO type DBBRR-A-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Length:

-   1-part:

500 mm / 750 mm / 1000 mm (-0500/-0750/-1000).

-   2-part:

1500 mm / 1750 mm / 2000 mm (-1500/-1750/-2000).

-	Air throw pattern:

-	one-way horizontal throw (-E).

-	two-way horizontal throw (-B, standard).

-	vertical throw (-V).

-	crosswise throw (-K).

-	Return air without blades (-O).

-	Material and paint (round duct):

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Blade colour:

-	Without blades (-00000, available only for return air).

-	With blades of plastic material:

-	Similar to RAL colour 9005 (black, standard) (-L9005).

-	Similar to RAL colour 9010 (white) (-L9010).

-  Blades made of aluminium painted to a freely selectable RAL colour (same colour as round duct) (-

Axxxx, always with 4 digits). (Painted blades cannot be adjusted subsequently.)

-	Number of slots:

-	2-slot (-02)

-	4-slot (-04)

-	6-slot (possible from NW 280 upwards) (-06)

-	8-slot (possible from NW 355 upwards) (-08)

-	10-slot (possible for NW 500) (-10)

-	12-slot (possible for NW 500) (-12)

-	14-slot (possible for NW 500) (-14)

-	Mounting position:

-	Horizontal throw to the right (3 o'clock) (-3U).

-	Vertical throw downward (6 o'clock) (standard) (-6U).

-	Horizontal throw to the left (9 o'clock) (-9U).

-	Vertical throw upward (12 o'clock) (-0U).

-	Hit-and-miss damper:

-	Without hit-and-miss damper (-SN).

-	With integrated hit-and-miss damper (-SS, standard) made of galvanised sheet steel, for simple air

volume and ductwork regulation.

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8

threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Rubber lip seal

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

KGRR

Round duct compact grille KGRR, for supply and return air, suitable for connection to DIN ducts. With integrated, manually adjustable hit-and-miss damper made of galvanised sheet steel, for simple air volume and ductwork regulation.

-   With horizontal, pivoting air deflection blades (adjustable at the front) and hit-and-miss damper.

Product: SCHAKO type KGRR-08-...

-   With vertical, pivoting air deflection blades (adjustable at the front) and hit-and-miss damper.

Product: SCHAKO type KGRR-15-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Length:

-   1-part:

500 mm / 750 mm / 1000 mm (-0500 / -0750 / -1000).

-   2-part:

1500 mm / 1750 mm / 2000 mm (-1500 / -1750 / -2000).

-	Height:

-	Grille height 65 mm (-065)

-	Grille height 115 mm (-115)

-	Grille height 215 mm (-215)

-	Grille height 315 mm (-315)

-	Air throw pattern:

-	Blade position straight (-L000) (standard).

-	Horizontal blade position, one-way right (-L00R) (KGRR-08-... only).

-	Horizontal blade position, one-way left (-L00L) (KGRR-08-... only).

-	Blade position 44° diverging (-L044).

-	Blade position 84° diverging (-L084).

-	Blade position opposite to one another (-LGEG).

-	Material and paint (round duct):

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-  Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Mounting position:

-	Horizontal throw to the right (3 o'clock) (-3U).

-	Vertical throw downward (6 o'clock) (standard) (-6U).

-	Horizontal throw to the left (9 o'clock) (-9U).

-	Vertical throw upward (12 o'clock) (-0U).

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8 threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Rubber lip seal (-GD0 / -GD1)

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

For more accessories, please refer to the separate brochure available upon request.

DSARR

Round duct nozzle jet diffuser DSARR-..., for supply air, suitable for connection to DIN ducts.

-   With fixed nozzles.

Product: SCHAKO type DSARR-F-...

-   With individually manually adjustable nozzles.

Product: SCHAKO type DSARR-V-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Length:

-   1-part:

500 mm / 750 mm / 1000 mm (-0500 / -0750 / -1000).

-   2-part:

1500 mm / 1750 mm / 2000 mm (-1500 / -1750 / -2000).

-	Material and paint (round duct):

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Nozzle colour:

-	Plastic similar to RAL colour 9005 (black, standard) (-DS).

-	Plastic similar to RAL colour 9010 (white).

-	Nozzle rows:

-	1 row of nozzles (-1, standard).

-	2 rows of nozzles (-2).

-	4 rows of nozzles (-4) (possible from NW 400).

-	Mounting position:

-	Horizontal throw to the right (3 o'clock) (-3U).

-	Vertical throw downward (6 o'clock) (standard) (-6U).

-	Horizontal throw to the left (9 o'clock) (-9U).

-	Vertical throw upward (12 o'clock) (-0U).

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8

threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Hit-and-miss damper:

-	Without hit-and-miss damper (standard) (-SN).

-	With integrated hit-and-miss damper (-SS) made of galvanised sheet steel, for simple air volume and

ductwork regulation.

-	Rubber lip seal

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

WGARR

Long throw nozzle grille with integrated round duct WGARR for supply air, suitable for connection to DIN ducts. With integrated, individually and manually adjustable nozzles, pivoting range 45°.

Product: SCHAKO type WGARR

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Length:

-   1-part:

500 mm / 750 mm / 1000 mm (-0500 / -0750 / -1000).

-   2-part:

1500 mm / 1750 mm / 2000 mm (-1500 / -1750 / -2000).

-	Material and paint (round duct):

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Nozzle colour:

-	Plastic similar to RAL colour 9006 (white aluminium) (-DA).

-	Plastic similar to RAL colour 9007 (grey aluminium) (-DG).

-	Plastic similar to RAL colour 9005 (black, standard) (-DS).

-	Plastic similar to RAL colour 9010 (white) (-DW).

-	Nozzle rows:

-	1 row of nozzles (-1).

-	2 rows of nozzles (possible from NW 400) (-2).

-	Mounting position:

-	Horizontal throw to the right (3 o'clock) (-3U).

-	Vertical throw downward (6 o'clock) (standard) (-6U).

-	Horizontal throw to the left (9 o'clock) (-9U).

-	Vertical throw upward (12 o'clock) (-0U).

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8

threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Hit-and-miss damper

-	Without hit-and-miss damper (standard) (-SN).

-	With integrated hit-and-miss damper (-SS) made of galvanised sheet steel, for simple air volume and

ductwork regulation.

-	Rubber lip seal:

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

Accessories for round duct system RR-COMPLETE

-	Dummy pipe (-BLR)

-	Pressed bend (-BGE)

-	Bent segment (-BSE)

-	Symmetric reduction piece (-USE)

-	Asymmetric reduction piece (-UAE)

-	T-piece 90° (-ATE)

-	Push-on rosette (SRO)

-	Straight end cover (-EG)

-	Connection sleeve (-MUF)

Dummy pipe BLR according to DIN EN1506, suitable for connection to DIN ducts.

Product: SCHAKO type BLR-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Length:

-   1-part:

500 mm / 750 mm / 1000 mm (-0500 / -0750 / -1000).

-   2-part:

1500 mm / 1750 mm / 2000 mm (-1500 / -1750 / -2000).

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

-	Fastening methods:

-	Without fastening hole (-B0).

-	With fastening hole ø11.5 (-BB, standard). (Prepared for suspended installation by using an M8

threaded rod and an M8 nut to be provided on site.)

Accessories (at an extra charge):

-	Rubber lip seal:

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

Pressed bend BGE, according to DIN EN1506, suitable for connection to DIN ducts.

Product: SCHAKO type BGE-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	Angle:

-	Angle 30° (-30).

-	Angle 45° (-45).

-	Angle 90° (-90).

Bends with different degree figures (a) are not available.

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

Accessories (at an extra charge):

-	Rubber lip seal:

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

Segment bend BSE, according to DIN EN1506, suitable for connection to DIN ducts.

Product: SCHAKO type BSE-...

-	Nominal width:

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Angle:

-	Angle 15° (-15).

-	Angle 30° (-30).

-	Angle 45° (-45).

-	Angle 60° (-60).

-	Angle 90° (-90).

Bends with different degree figures (a) are not available.

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

Accessories (at an extra charge):

-	Rubber lip seal:

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

Symmetric reduction piece USE, according to DIN EN1506, suitable for connection to DIN ducts.

Product: SCHAKO type USE-...

-	Nominal width:

-	NW 224-200 (-224-200)

-	NW 250-200 (-250-200)

-	NW 280-200 (-280-200)

-	NW 315-200 (-315-200)

-	NW 315-250 (-315-250)

-	NW 355-250 (-355-250)

-	NW 400-250 (-400-250)

-	NW 400-315 (-400-315)

-	NW 450-280 (-450-280)

-	NW 450-315 (-450-315)

-	NW 500-315 (-500-315)

-	NW 500-400 (-500-400)

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

Accessories (at an extra charge):

-	Rubber lip seal:

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

Asymmetric reduction piece UAE, according to DIN EN1506, suitable for connection to DIN ducts.

Product: SCHAKO type UAE-...

-	Nominal width:

-	NW 224-200 (-224-200)

-	NW 250-200 (-250-200)

-	NW 280-200 (-280-200)

-	NW 315-200 (-315-200)

-	NW 315-250 (-315-250)

-	NW 355-250 (-355-250)

-	NW 400-250 (-400-250)

-	NW 400-315 (-400-315)

-	NW 450-280 (-450-280)

-	NW 450-315 (-450-315)

-	NW 500-315 (-500-315)

-	NW 500-400 (-500-400)

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-   Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

Accessories (at an extra charge):

-	Rubber lip seal:

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

T-piece ATE, according to DIN EN1506, suitable for connection to DIN ducts.

Product: SCHAKO type ATE-...

-	Nominal width:

-	NW 200-200 (-200-200)		-	NW 355-250 (-355-250)

-	NW 200-250 (-200-250) 		-	NW 355-315 (-355-315)

-	NW 200-315 (-200-315) 		-	NW 355-355 (-355-355)

-	NW 224-224 (-224-224) 		-	NW 355-500 (-355-500)

-	NW 224-250 (-224-250) 		-	NW 400-200 (-400-200)

-	NW 224-315 (-224-315)		-	NW 400-250 (-400-250)

-	NW 250-200 (-250-200) 		-	NW 400-315 (-400-315)

-	NW 250-250 (-250-250) 		-	NW 400-400 (-400-400)

-	NW 250-315 (-250-315) 		-	NW 400-500 (-400-500)

-	NW 250-400 (-250-400) 		-	NW 450-250 (-450-250)

-	NW 280-200 (-280-200) 		-	NW 450-315 (-450-315)

-	NW 280-280 (-280-280) 		-	NW 450-450 (-450-450)

-	NW 280-400 (-280-400) 		-	NW 450-500 (-450-500)

-	NW 315-200 (-315-200) 		-	NW 500-200 (-500-200)

-	NW 315-250 (-315-250) 		-	NW 500-250 (-500-250)

-	NW 315-315 (-315-315) 		-	NW 500-315 (-500-315)

-	NW 315-400 (-315-400) 		-	NW 500-400 (-500-400)

-	NW 315-500 (-315-500) 		-	NW 500-500 (-500-500)

-	NW 355-200 (-355-200)

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

Accessories (at an extra charge):

-	Rubber lip seal:

-	Without rubber lip seal (-GD0) (standard).

-	With rubber lip seal (-GD1), on both sides, made of EPDM.

Push-on rosette SRO, suitable for connection to DIN ducts.

Product: SCHAKO type SRO-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

Straight end cover EG, suitable for connection to DIN ducts.

Product: SCHAKO type EG-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-   Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).

Connection sleeve MUF, suitable for connection to DIN ducts.

Product: SCHAKO type MUF-...

-	Nominal width:

-	NW 200 (-200)

-	NW 224 (-224)

-	NW 250 (-250)

-	NW 280 (-280)

-	NW 315 (-315)

-	NW 355 (-355)

-	NW 400 (-400)

-	NW 450 (-450)

-	NW 500 (-500)

-	Width:

-	70 mm (-070) (connecting round duct/round duct, dummy pipe/dummy pipe).

-	75 mm (-075) (connecting round duct/dummy pipe with connecting piece d200-d224).

-	80 mm (-080) (connecting connecting piece/connecting piece d200-d224).

-	95 mm (-095) (connecting round duct/dummy pipe with connecting piece d250-d355).

-	115 mm (-115) (connecting round duct/dummy pipe with connecting piece d400-d500).

-	120 mm (-120) (connecting connecting piece/connecting piece d250-d355).

-	160 mm (-160) (connecting connecting piece/connecting piece d400-d500).

-	Material and paint:

-	Galvanised sheet steel (-SV-000) (at an extra charge).

-	Sheet steel (-SB-...):

-	Painted to the RAL colour 9010 (white, standard) (-9010).

-	Painted to a freely selectable RAL colour (-xxxx, always with 4 digits).