Volumetric flow controller VAQS®

Specification texts

Volumetric flow controller in rectangular design, for duct connection to DIN EN 1505, for use in supply and return air systems for constant or variable volumetric flow, room or duct pressure regulation. With positive control Vmin, Vmax or "CLOSED". Allowed pressure difference range: 50-1000 Pa, allowed ambient temperature 0-50°C. Suitable for use with duct velocities of 1-12 m/s.

It is possible to subsequently adjust the manufacturer set operation volume flow. The output signal can be used for master/slave or parallel operation of several controllers or for actual value display 2-10 V DC (0-10 V DC), which corresponds to 0-100 % of the set Vnenn in DDC/ZLT systems.

Housing made of galvanised sheet steel. Opposed blades, blades sealing air-tight to DIN EN 1751, class 4 (class 3 up to a height of 500), housing leakage air flow to DIN EN 1751, class C, at a duct pressure up to 1000 Pa, made of aluminium. Measuring rods made of aluminium, blade support made of plastic, position-independent installation possible. With electric controller LMV/NMV-D3-MF, control voltage 24 V AC, 50 / 60 Hz, requirement: measuring air 0...+50°C/5...95% rH, non-condensing, wired and adjusted in-factory. Right-hand design.

Product: SCHAKO type VAQS®

Housing (at an extra charge):

-	galvanised sheet steel with DD coating (-DD)

Accessories (at an extra charge):

-	Acoustic cladding (-DS2) made of 20 mm sound-absorbing material with sheet metal casing made of galvanised sheet steel, non-flammable according to DIN 4102-17. Includes M6 cage nuts at the corner angles.

-	Mineral wool silencer (-ZSQ) with M2 Metu profile on both sides, housing (L=1500) consisting of galvanised sheet steel with integrated MWK-OB silencing baffles (L=1000). The MWK-OB silencing baffles, with RAL quality seal, consist of abrasion-resistant mineral fibre boards covered with fibre glass filament (biosoluble, non-flammable to DIN 4102) in a frame of galvanised sheet steel. Baffles measured to ISO/DIS 7235 and to DIN 45646.

-	Setting and diagnostic device ZTH-EU (Belimo)

-	MP-bus-capable electric controller LMV-D3-MP, NMV-D3-MP