Volumetric Flow Controller Model VRA-R Smart®

Specification texts

Volumetric flow controller in round design, for spiral duct connection to DIN EN 1506, for use in supply and return air systems for constant or variable volumetric flow, room or duct pressure regulation. With positive control Vmin, Vmax or "CLOSED". Allowed pressure difference range: 20-1000 Pa, allowed ambient temperature 0-50°C. Suitable for use with duct velocities of 1-12 m/s.

It is possible to subsequently adjust the manufacturer set operation volume flow. The output signal can be used for master/slave or parallel operation of several controllers or for actual value display 2-10 V DC (0-10 V DC), which corresponds to 0-100 % of the set Vmax in DDC/ZLT systems.

Housing made of galvanised sheet steel with silicone-free damper leaf seal made of PUR (airtight to DIN EN 1751 (NW100 Class 2 / NW125 - 400 Class 3), housing leakage class B to DIN EN 1751), measuring rods made of extruded aluminium profile, damper bearing made of brass. With electric controller LMV-D3-MF, control voltage 24 V AC, 50 / 60 Hz, temperature compensation of 10-40°C, wired and adjusted in-factory.

Product: SCHAKO type VARS®

Housing (at an extra charge):

-	galvanised sheet steel with DD coating (-DD)

-	Stainless steel (-V2A)

-	Stainless steel (-V4A)

Accessories (at an extra charge):

-	Flat-bed acoustic cladding (-FD1), made of 3 mm sound-absorbing material with sheet metal casing made 	of galvanised sheet steel.

-	Acoustic cladding (-DS2) made of 20 mm sound-absorbing material with sheet metal casing made of 	galvanised sheet steel, non-flammable according to DIN 4102-17.

-	Metu flange (-MF1/-MF2), on both sides, duct flange AF.

-	Counter flange, on both sides, to Metu flange (pair), loose.

-	Tension ring (-SR) to connect Metu flange to counter flange (pair), loose.

-	Flat flange (-FF1/-FF2), on both sides, to DIN 24 154 / 5.

-	Rubber lip seal (-GD1), made of special rubber.

-	Duct silencer (-RS), casing and perforated sheet made of galvanized sheet steel with mineral wool filling

-	Setting and diagnostic device ZTH-EU (Belimo)

-	Electric controller with MP bus capability

Please note!

Tension rings, counter flanges and duct silencers must be ordered separately and are supplied loose!