Sound-damped volumetric flow controller VAS

Specification Text

Sound-damped volumetric flow controller for use in supply or return air systems. Connection to rectangular duct connec-tions to DIN EN 1505 without reduction or transition piece; connection to ductwork to DIN EN 1506 is possible using a transition piece. Volumetric flow controller for controlling constant or variable volumetric flows and for room or duct pressure regulation. With positive control Vmin, Vmax or "CLOSED". Available as right-hand and left-hand models.

Allowed ambient temperatures: 0 - 55°C. It is possible to subsequently adjust the manufacturer-set operating volu-metric flow at any time. The actual throughput of the volu-metric flow can be measured via the U5 signal. The output signal can be used for master/slave or parallel operation of several controllers or for actual value display 2-10 V DC (0-10 V DC), which corresponds to 0-100 % of the set Vnenn in DDC/ZLT systems.

The VAS fulfills the most stringent tightness requirements as defined by DIN EN 1751. Housing leakage, class C and dam-per leaf leakage, class 4. The housing consists of galvanised steel (-SV) with thermo-acoustic insulation and hygienic mi-neral wool to VDI 6022 and a damper made of extruded alu-minium profile with a TPV rubber seal. The differential pres-sure signal is measured by a measuring cross made of alu-minium profiles and is evaluated in the electronic controller.

-	For use in supply air systems, with electric controller NMV-D3-MP SO, control voltage 24 V AC, 50 / 60 Hz, temperature compensation of 10-40°C, wired and ad-justed in-factory.

Product: SCHAKO type VAS-K-…-Z or type VAS-S-…-Z with extended silencer unit

-	For use in return air systems, with electric controller NMV-D3-MP SO, control voltage 24 V AC, 50 / 60 Hz, temperature compensation of 10-40°C, wired and ad-justed in-factory.

Product: SCHAKO type VAS-K-…-A or type VAS-S-…-A with extended silencer unit

Mounting direction:

-	right (-R) (standard)

-	left (-L)

Accessories (at an extra charge):

-	Flat-bed acoustic cladding (-FD1), for reducing the radia-ted noise, made of sound-absorbing material arranged inside the housing, thus same outer dimensions.

-	Heating register (-H2/-H4): with connection via an exter-nal thread, operating pressure 8 bar, test pressure 16 bar, consisting of galvanised sheet steel frame, copper pipes, steel collector, aluminium blades.

- with 2 rows of pipes (-H2)

- with 4 rows of pipes (-H4)

-	DD coating (-DD) against aggressive return air

-	Transition piece, high-pressure side, made of galvanised sheet steel

- for connection to round ducts (-USR)

- for connection to rectangular ducts (-USE)

-	Rubber lip seal (-GD1) made of special rubber (for USR only).