ATEX volumetric flow controller VQEX

Specification text

VQEX

Volumetric flow controller made of galvanised sheet steel in rectangular design, for duct connection to EN 1505, for use in supply and return air systems for constant or variable volu-metric flow regulation, ATEX version available in accordance with product directive ATEX 2014/34/EU.

Allowed differential pressure range: 50-1000 Pa.

Allowed ambient temperature: 0…50° C.

For use with duct velocities of 2...13 m/s.

It is possible to subsequently adjust the manufacturer set ope-ration volume flow.

The output signals 0/2…10 V DC can be used for actual value display and for display of the damper position.

Housing made of galvanised sheet steel:

Opposed blades, air-tight to DIN EN 1751, up to Class 4, made of extruded aluminium profile, sintered bearing

Product: SCHAKO type VQEX-JK-LU

Opposed blades, not airtight, made of galvanised sheet steel, Sintered bearing

Product: SCHAKO Type VQEX-HKU

Housing leakage according to DIN EN 1751, class B

Aluminium measuring rods in which for measuring the average values 6 measuring points each have been attached to the pressure and suction sides, using the median line method.

Damper bearing: sintered bearing

With electric controller, ATEX-NM-K2,

Supply voltage: 24 V AC/DC ±15 %, 50/60 Hz

wiring and adjusting by manufacturer

Product: SCHAKO Type VQEX

with spring return actuator (at an extra charge)

--- currentless CLOSED

--- currentless OPEN

Casing (at an extra charge) made of:

--- galvanised sheet steel with DD coating  (-DD)

ACCESSORIES VQEX

Acoustic cladding (-DS 4)

made of sound-absorbing, insulating 40 mm material with sheet steel covering made of galvanised sheet steel, non-flammable according to DIN 4102-17. In this model, each corner angle contains an M6 cage nut

Mineral wool silencer (-ZSQ-EX)

Galvanised sheet steel housing

M3 metu profile on both sides.

Baffle frame made of galvanised sheet steel

Mineral fibre boards according to DIN 4102 A2, with glass filament cover, biosoluble, wear-resistant

with baffles MWK

ATTENTION

The additional silencer is not included in the order code of the volumetric flow controllers and must be ordered separately.