Volumetric flow controller VRAPPs

Specification texts

Volumetric flow rate controllers for use in supply/return air systems for constant or variable volume flow, room or duct pressure control. Also suitable for use in digesters or with air containing aggressive media. With positive control Vmin, Vmax or "CLOSED". Permitted pressure difference range: 20-1000 Pa, permitted surrounding temperatures 0-55° C. For use with duct velocities of 1-12 m/s (only Gruner 227 VM). It is possible to subsequently adjust the ex-factory set operational volumetric flows (type Gruner, setting directly at the controller via the potentiometer without Service tool). The output signal can be used for      master/slave or parallel operation of several controllers or for actual value display 2-10 V DC which corresponds to 0-100 % of the set Vmax or 0(2)-10 V which corresponds to 0-100% of Vnenn in DDC / ZLT systems.

Housing made of plastic PPs. Damper blade, damper axle and measuring cross made of plastic PP. Controller and drive console made of plastic PP. With electric controller (227VM-024-10-DS3), control voltage 24 V AC, 50/60 Hz, temperature compensation of 10-40 °C, wired and adjusted ex factory.

Damper blade seal silicone-free made of PUR (NW 110 sealing airtight to DIN EN 1751 Class 2, NW 125 - 400 sealing airtight to DIN EN 1751 Class 3).

Housing tightness class C to DIN EN 1751.

Product: SCHAKO type VRAPPs

Size ........................

-	with Gruner compact controller (standard)

-	227VM-024-10-DS3

-	with Gruner universal controller GUAC-SM3/SCH (at an extra charge)

-	328CS-024-10B-VISIT06 (with high-speed damper drive)

-	361C-024-10-V (spring return actuator)

- currentless CLOSED

- currentless OPEN

-	with MP-bus-capable controller (at an extra charge)

VRP-M-VFP300 / NM24A-V-ST

-	with high-speed actuator drive (at an extra charge)

VRP-M-VFP 300 / NMQ24A-SRV-ST

-	with spring return actuator (at an extra charge):

VRP-VFP 300 / SF24A-V

VRP-M-VFP 300 / SF24A-V-ST (MP-bus-capable)

-	currentless "CLOSED"

-	currentless "OPEN"

Accessories (at an extra charge):

-	Flat flange (pair), on both sides, made of plastic PPs (-FF3)