Volumetric flow controller VRAPPs

Specification texts

Volumetric flow rate controllers for use in supply/return air systems for constant or variable volume flow, room or duct pressure control. Also suitable for use in digesters or with air containing aggressive media. With positive control Vmin, Vmax or "CLOSED". Permitted pressure difference range: 20-1000 Pa, permitted surrounding temperatures 0-55° C. For use with duct velocities of 1-12 m/s (only Gruner 327 VM). It is possible to subsequently adjust the ex-factory set operational volumetric flows (type Gruner, setting directly at the controller via the potentiometer without service tool). The output signal can be used for master/slave or parallel operation of several controllers or for actual value display 2-10 V DC which corresponds to 0-100 % of the set Vmax or 0(2)-10 V which corresponds to 0-100% of Vnenn in DDC / ZLT systems.

Housing made of plastic PPs. Damper blade, damper axle and measuring cross made of plastic material PP. Controller and drive console made of plastic PP. Damper blade seal silicone-free made of PUR (NW 110 sealing airtight to DIN EN 1751 Class 2, NW 125 - 400 sealing airtight to DIN EN 1751 Class 3).

Housing tightness class C to DIN EN 1751.

Product: SCHAKO type VRAPPs

Nominal width:

-	NW 110 (-110)

-	NW 125 (-125)

-	NW 160 (-160)

-	NW 200 (-200)

-	NW 250 (-250)

-	NW 315 (-315)

-	NW 400 (-400)

Attachment assembly:

-	with electric controller – standard

-	Gruner:

-	327VM-24-10-DS4-MB, compact (-A164), 10 Nm

-	with electric controller - alternative

-	Belimo:

-	VRU-M1-BAC, NM24A-VST (-A151), 10 Nm

-	VRU-M1-BAC, NMQ24A-VST (-A154), 8 Nm

-	VRU-M1-BAC, NKQ24A-VST (-A155), 8 Nm

-	VRU-M1-BAC, NF24A-VST (-A156), 10 Nm

-	VRU-M1R-BAC, NMQ24A-VST (-A159) 8 Nm

-	Sauter:

-	ASV215BF132E, compact (-A138), 10 Nm

-	ASV215BF152E, compact (-A139), 10 Nm

-	Gruner:

-	GUAC-SM3/SCH, 361C-024-10-V (-A069), 10 Nm

-	GUAC-SM3/SCH, 328CS-024-10B-V/ST06 (-A071), 10 Nm

-	GUAC-PM3/SCH, 341C-024-10-V (-A073), 10 Nm

-	GUAC-PM3/SCH, 328CS-024-10B-V/ST06 (-A075), 10 Nm

-	327VM-024-10-DS6-MB, compact (-A167), 10 Nm

-	with pneumatic controller – standard

-	Sauter:

-	RLP100 F003, AK42P F003 (linear drive) (-A107), 200 N

-	with pneumatic controller - alternative

-	Sauter:

-	RLP100 F914, AK42P F003 (linear drive) (-A109), 200 N

-	RLP100 F123, AK42P F003 (linear drive) (-A111), 200 N

Mode:

-	0-10 V (-0)

-	2-10 V (-2) (pneumatic controllers can only be delivered in mode 2!)

Volumetric flow set value Vmin/Vkon:

-	ex-works, according to table (-0000)

-	Value in m³/h (-xxxx) (always with 4 digits)

Volumetric flow set value Vmax:

-	ex-works, according to table (-0000)

-	Value in m³/h (-xxxx) (always with 4 digits)

Damper position:

-	no spring return actuator (standard) (-NA)

-	currentless OPEN (-N0), only for actuators with spring return

-	currentless CLOSED (-NC), only for actuators with spring return

Please note!

Counter flanges and duct silencers must be ordered separately!

Accessories (at an extra charge):

-	Flange (-KA0/-FF3) (duct connection)

-	without flange, butted (-KA0) (standard)

-	with flat flange (pair), on both sides, made of plastic material PPs (-FF3)