Volumetric flow controller VRAQ

Specification texts

Volumetric flow controller in rectangular design, for spiral duct connection to DIN EN 1505 / DIN 24190, for use in supply and return air systems for constant or variable volumetric flow, room or duct pressure regulation. With positive control Vmin, Vmax or "CLOSED". Allowed pressure difference range: 50-1000 Pa, allowed ambient temperature 0...+50°C. Suitable for use with duct velocities of 1-12 m/s. It is possible to subsequently adjust the operating volumetric flows set ex works. Can be fitted position-independently. The output signal can be used for master/slave or parallel operation of several controllers or for actual value display 2-10 V DC (0-10 V DC), which corresponds to 0-100% of the set Vmax in DDC / ZLT systems (for more information, please refer to technical data sheet GUAC-SM3/SCH Universal and 327VM-... Compact from Gruner). Housing made of galvanised sheet steel. Opposed blades, made of galvanised sheet steel, not sealing airtight, with plastic bearing. Measuring cross made of extruded aluminium profile, measuring cross support made of plastic (PA6). Right-hand design. With electric controller, control voltage 24 V AC, 50/60 Hz, requirement: measuring air 0 °C to 50 °C/5-95% relative humidity, non-condensing, wired and adjusted in-factory. TÜV inspected according to VDI 6022 Sheet 1.

Product: SCHAKO type VRAQ-HP

-   Opposed blades, made of galvanised sheet steel, not sealing airtight, with sintered bearing.

Product: SCHAKO type VRAQ-HU

-   Opposed blades made of extruded aluminium profile, sealing air-tight to DIN EN 1751, up to class 4, with

plastic bearing.

Product: SCHAKO type VRAQ-JP

-   Opposed blades made of extruded aluminium profile, sealing air-tight to DIN EN 1751, up to class 4, with

sintered bearing.

Product: SCHAKO type VRAQ-JU

-	 Housing leakage according to DIN EN 1751, class C, at a duct pressure of up to 1000 Pa.

-   Leakage with closed blades according to DIN EN 1751, up to class 4 at a duct pressure of up to 1000 Pa

(VRAQ-JP / VRAQ-JU... only).

Higher requirements upon request.

-	 Housing (at an extra charge) made of:

-   galvanised sheet steel with DD coating (-DD) (not possible for VRAQ-JP / VRAQ-JU)

-	with spring return actuator (at an extra charge)

-	currentless "CLOSED" (-NC)

-	currentless "OPEN" (-NO)

With pneumatic drive correspondingly depressurised OPEN / depressurised CLOSED.

-	with pneumatic controller, feed pressure 1.2 ± 0.1 bar, for use with duct velocity 3-12 m/s:

-	depressurised "CLOSED" or

-	Depressurised "OPEN"

For controller selection (attachment assembly), see page 43.

Accessories (at an extra charge):

-	Acoustic cladding (-DS4) made of 40 mm (pressed to 35 mm) sound-absorbing material, with sheet metal

casing made of galvanised sheet steel, non-flammable to DIN 4102-17, including M8 cage nuts.

-	Mineral wool silencer (-ZSQ) with M3 Metu profile on both sides, housing (L=1500) consisting of

galvanised sheet steel with integrated MWK-OB silencing baffles (L=1000). The MWK-OB silencing baffles

with RAL quality seal consist of abrasion-resistant mineral fibre boards covered with fibre glass filament

(biosoluble, non-flammable to DIN 4102 A2) in a frame of galvanised sheet steel. Baffles measured to

ISO/DIS 7235 and to DIN 45646.