ATEX volumetric flow controller VREX

Specification text

Volumetric flow controller made of galvanised sheet steel in round design, for spiral duct connection, for use in supply and return air systems for constant or variable volumetric flow re-gulation. Suitable for room or duct pressure control. ATEX ver-sion available in accordance with product directive ATEX 2014/34/EU.

Allowed differential pressure range: 0-1000 Pa.

Allowed ambient temperature 0…50°C.

For use with duct velocities of 2-13 m/s.

It is possible to subsequently adjust the manufacturer set ope-ration volume flow.

The output signals 0/2…10 V DC can be used for actual value display and for display of the damper position.

Housing made of galvanised sheet steel with damper blade se-al free of silicone made of PUR for airtight sealing to DIN EN 1751 (Class 2 NW 100 only, Class 3 NW 125 - 400 only), housing leakage class B according to DIN EN 1751.

Aluminium measuring rods in which for measuring the average values 6 measuring points each have been attached to the pressure and suction sides, using the median line method.

Damper bearing made of brass

With electric controller, with integrated precision pressure sen-sor for differential pressure measurement.

Supply voltage: 24 V AC/DC ± 15% (20.4…27.6 VAC/DC),

50/60 Hz

wiring and adjusting by manufacturer.

Product: SCHAKO type VREX

-	with spring return actuator (at an extra charge)

--- currentless CLOSED

--- currentless OPEN

-	Housing (at an extra charge) made of:

--- Galvanised sheet steel, with DD coating (-DD)

--- Stainless steel 1.4301 (-V2A)

--- Stainless steel 1.4571 (-V4A)

Accessories for VREX

Metu flange (-MF1, MF2)

-	on both sides, duct flange type MF1, galvanised steel

-	on both sides, duct flange type MF2, stainless steel V2A, 1.4301

Counter flange (-GF) (pair), loose

-	on both sides, to Metu flange (must be ordered separately)

Tension ring (-SR) (pair), loose

-	to connect Metu flange to counter flange (must be ordered separately) Flat flange (-FF1, FF2)

-	on both sides, according to DIN 24 154/5. type FF1, galvani-sed steel

-	on both sides, according to DIN 24 154/5. type FF2, stainless steel V2A, 1.4301

Acoustic cladding (-DS 2)

-	made of sound-absorbing, insulating 20 mm material with sheet steel covering made of galvanised sheet

steel, non-flammable according to DIN 4102-17.

Flat-bed acoustic cladding (-FD1)

-	made of sound-absorbing, insulating 3 mm material with sheet steel covering made of galvanised sheet

steel (stan-dard)

Rubber lip seal (-GD1)

-	on both sides, special rubber.

Duct silencer (-RS-Ex)

-	rigid model

-	Outer jacket and perforated plate made of galvanised sheet steel

-	mineral wool filling

Please note!

Counter flanges, tension rings or duct silencers must be or-dered separately and are supplied loose!